## ReadMe
THIS DRAFT DOCUMENT WAS DEVELOPED BY THE STATEWIDE UTILITY CODES AND STANDARDS ENHANCEMENT (CASE) TEAM
The California Statewide Codes and Standards Enhancement (CASE) Program is funded in part by California utility customers under the auspices of the California Public Utilities Commission. Copyright 2025 Pacific Gas and Electric Company, Southern California Edison, San Diego Gas & Electric Company. All rights reserved, except that this document may be used, copied, and distributed without modification. Neither Pacific Gas and Electric Company, Southern California Edison, San Diego Gas & Electric Company, or any of its employees make any warranty, express or implied; or assume any legal liability or responsibility for the accuracy, completeness or usefulness of any data, information, method, product, policy or process disclosed in this document; or represent that its use will not infringe any privately-owned rights including, but not limited to, patents, trademarks or copyrights.
Introduction
The information in the tabs of this spreadsheet describe a proposed building energy model prototype for Indoor Controlled Environment Horticulture facilities with high lighting intensities, such as indoor cannabis farms. This prototype is being considered for inclusion in the 2028 Alternative Calculations Methods (ACM) and the 2028 version of California's Building Energy Code Compliance Software (CBECC).
The proposed prototype would be applicable only for Indoor CEH Buildings (those with <50% skylight ratio) that have at least one room with lighting power density above 30W per canopy square foot.
Building Energy Model Prototypes
Building energy model prototypes represent typical building types within the state and incorporate minimum energy efficiency and load management requirements from California's Energy Code (California Code of Regulations, Title 24, Part 6).
Prototypes are used as the standard design (baseline) model for the performance method of complying with Building Energy Efficiency Standards. The performance method provides flexibility to trade-off the energy performance of different components to achieve compliance. When a proposed design is modeled, compliance is demonstrated if the overall energy performance is equal to or better than the standard design's performance.
The impact of proposed code change measures is also evaluated in energy models of these prototype buildings, and statewide impacts of measures are estimated based on the statewide distribution of each building type by climate zone. These prototypes include general building characteristics, such as layouts and zones, and building envelope and space-type specific characteristics, such as HVAC system, ventilation, lighting intensity, lighting schedules, occupancy schedules, plant transpiration schedules, temperature setpoint schedules, and humidity setpoint schedules.
The Proposed Indoor CEH Building Prototype
The proposed Indoor CEH building prototype will introduce new horticulture-specific space types, commonly found in high-lighting intensity indoor farms. These new space types include cloning, vegetative, and flowering rooms for different stages of plant growth, as well as a plant drying room and a processing room for trimming, packaging, and other processing.
Why is an Indoor CEH Building Prototype Being Developed?
The Statewide CASE Team receives feedback from the public and other stakeholders throughout the code-development process. Recent stakeholder feedback suggested that Indoor (<50% skylight ratio) CEH building permit applicants are using the existing prototypes, such as “Conditioned Warehouse,” to show compliance via the performance path. However, none of the existing prototypes currently available in CBECC include the energy intensive process loads that are characteristic of indoor CEH buildings including rooms with lighting power density greater than 30 Watts per canopy square foot. To provide an option for the performance path that more accurately represents the loads in these facilities, the Statewide CASE Team, in conjunction with subject matter experts and a California Building Energy Modeling (CalBEM) Prototypes Technical Advisory Group, developed this Indoor CEH prototype. The assumptions were informed by field monitoring and data from cannabis farms throughout CA and the rest of the country.
Feedback on the Proposed Prototype
The Statewide CASE Team is requesting feedback on the proposed Indoor CEH building energy model prototype assumptions for indoor (<50% skylight ratio) CEH facilities that include a room with lighting power density greater than 30 Watts per canopy square foot. We invite participation from new and existing stakeholders.
Please send an email to amydroitcour@2050partners.com or garthtorvestad@2050partners.com and copy info@title24stakeholders.com with feedback or to set up a meeting to discuss feedback.

## Prototype
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
Controlled Environment Horticulture
Characteristic | Value | Data Sources
Building Type | Indoor Controlled Environmental Horticulture - Cannabis | Over 90% of Indoor CEH was estimated to be cannabis in the T24 2025 cycle
Building Category | Nonresidential
Vintages | 2 Vintages: Pre-2022 New Construction (2025+) | Based on year CEH became part of T24 NonRes-Vintage bins-Draft Report-30Nov2023-Final.docx
Shape | Rectangle | Previous CEH Floor plans. Previous T24 CASE work.
Total Floor Area (ft²) | 25,620 (244 ft x 105 ft) | Based Department of Cannabis License data by size.
Aspect Ratio | 2.3143 | Based Department of Cannabis License data by size.
Number of Floors | 1 | Based on 2050 CEH Prototype and Existing Warehouse Prototype. 2050 CEH Prototype assumption was based on CEH SME input.
Roof type | Flat | Based on 2050 CEH Prototype and Existing Warehouse Prototype. 2050 CEH Prototype assumption was based on CEH SME input.
Window-to-Wall Ratio (WWR) | 0% | When included, assuming high security feature in addition to T24 compliant windows, still researching this topic.
Shading Geometry | No Shades | Based on typical indoor horticulture buildings
Floor to floor height (ft) | 18 | Based on input from SME Kelly Energy Management, confirmed to be typical by other CEH SMEs.
Floor to ceiling height (ft) | 14 | Based on input from SME Kelly Energy Management, confirmed to be typical by other CEH SMEs.
Glazing sill height (ft) | n/a | Assuming high security feature in addition to T24 compliant windows, still researching this topic. For the time being assuming there 0 windows in this building for security reasons. Practically speaking the office areas would likely have a WWR similar to the small or medium office prototype and the corresponding sill height only in that office area not in the other parts of the building of the CEH prototype.

## Zones
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
Proposed Layout - Controlled Environment Horticulture
Space Type | Space/Thermal Zone | Conditioned (Y/N) | HVAC zone | Area Fraction | Area (ft²) | Length (ft) | Width (ft) | Volume (ft³) | Multipliers | Number of People | People (Persons/1,000 ft²) [T24, 2025, Table 120.1-A] | Canopy area | Notes
Horticulture_Vegetative | Horticulture_Vegetative | Y | Horticulture_Vegetative | 11.52% | 2940 | 20 | 147 | 41160 | 1 | 0 | - | 4116 | The veg/clone room has two tiers for growing, thus double the canopy are per room square foot.
Horticulture_Flowering | Horticulture_Flowering 3 zones | Y | Horticulture_Flowering 3 HVAC zones | 48.97% | 12495 | 85 | 147 | 174930 | 1 | 0 | - | 8746.5 | The flowering space type needs to be split into 3 flowering rooms, with shifted schedules (a 9-week grow cycle starting every 3 weeks), each a separate HVAC zone.
Processing Area | Processing Area | Y | Processing | 8.23% | 2100 | 28 | 75 | 29400 | 1 | 3 | 1.4 | N/A | The processing area includes trimming, which generates a lot of dust and pollen
Horticulture_Drying | Drying room | Y | Horticulture_Drying | 5.879% | 1500 | 20 | 75 | 21000 | 1 | 0 | 0 | N/A
Storage | Storage and Shipping | Y | Storage | 9.594% | 2448 | 15 | 75 | 34272 | 1 | 0 | 0 | N/A
|  | Y |  |  |  | 63 | 21 |  |  |  |  | N/A
Office | Office | Y | Office_Area | 12.35% | 3150 | 42 | 75 | 44100 | 1 | 15.75 | 5 | N/A | Low density occupancy relative to office buildings.
Restrooms | Restrooms | Y | Office_Area | 1.646% | 420 | 20 | 21 | 5880 | 1 | 1 | - | N/A
Security office | Security office | Y | Office_Area | 1.811% | 462 | 22 | 21 | 6468 | 1 | 1 | 5 | N/A
Total (10 Spaces, 8 space types) | Total (10 Thermal Zones) |  | Total (8 HVAC Zones) | 100% | 25515 |  |  | 357210 |  |  |  | 12862.5
Estimated canopy area | 13000 | Based on department of cannabis data | Building Area | 25515
|  |  |  | 243 | 105
|  |  |  | Width (ft) | Length (ft)
Background Data [To be deleted prior to publication]
N
This tab provides a breakdown of the prototype space into the different space types and HVAC zones. The Statewide CASE Team would appreciate input on the area fraction of the different space types and thermal zones.

## Envelope
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
Envelope - Controlled Environment Horticulture
Element | Prototype | Assembly Type | Construction | Thermal properties | Vintage | Selected T24 | Note | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | CEH | Metal Building | Metal surface + Continuous Insulation + Gypsum board | U-factor IP | Pre 2022 | 2001 | ASHRAE 90.1, 2022 Table A3.4.3.1, 3.5", R-0 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292 | 0.292
[5 empty] | 2022+ | 2025 | Table 140.3-B | 0.098 | 0.053 | 0.098 | 0.053 | 0.053 | 0.098 | 0.098 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053
Roof | CEH | Metal Roof | Roof Membrane + Continuous Insulation + Metal Decking | U-factor IP | Pre 2022 | 2001 | Table 1-H | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065
[5 empty] | 2022+ | 2025 | Table 140.3-B | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038
Windows | Windows | Fixed Windows | Single Pane (CBECS 2018, ~ 50 % of warehouseconversion that were built before 2000 are single pane) | U-factor IP | Pre 2022 | 2001 | Table 1-H | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49
|  |  | Double Pane |  | 2022+ | 2025 | From Medium Office scorecard. Assumed windows only in office areas. This u-factor does not yet include security feature. | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
| Windows | Fixed Windows | Single Pane (CBECS 2018, ~ 50 % of warehouseconversion that were built before 2000 are single pane) | SHGC | Pre 2022 | 2001 | Table 1-H | 0.49 | 0.47 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.47 | 0.47 | 0.47 | 0.47 | 0.46 | 0.46 | 0.49
|  |  | Double Pane |  | 2022+ | 2025 | From Medium Office scorecard. Assumed windows only in office areas. This u-factor does not yet include security feature. | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Infiltration
[5 empty] | Vintage | I_75 (cfm/ft2) 6-sdied Infiltration rate @ 75 pa | Source | I-design (cfm/ft²) (4-sided Infiltration rate at normal pressure) (Design flow rate approach and Flow/Exterior Wall Area calculation method)
|  |  |  | Infiltration | Pre 2022 | 1.1 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B) | 0.76841
[5 empty] | 2022+ | 0.6 | 2022 CASE report (Table 38) & T24, 2025 (Table 140.3-B) | 0.41913
Source: T24 air barrier requirements (all editions) , the standardized infiltration rate reported in the 2022 CASE report, and Dodge 2023 data
Infiltration_rate_report_14May2025-Short-Version.docx
[7 empty] | Assumptions | [7 empty] | I design6 | cfm @ 10mph | I design 4
[7 empty] | Height - floor to ceiling | 14 | [5 empty] | 1.1 | 0.1232 | 1200.4608 | 0.76841
[7 empty] | Area | 25515 | [5 empty] | 1.1 | 0.1232 | 1200.4608 | 0.76841
[7 empty] | Perimeter | 696 | [5 empty] | 1.1 | 0.1232 | 1200.4608 | 0.76841
[7 empty] | Building 4 sided floor area= | 9744 | [5 empty] | 1 | 0.112 | 1091.328 | 0.69855
[7 empty] | Building 6 sided floor area= | 60774 | [5 empty] | 0.6 | 0.0672 | 654.7968 | 0.41913
[7 empty] | 6 sided /4 sided factor= | 6.2371
0.112
This tab provides envelope assumptions, consistent with Title 24, Part 6 requirements for a metal building. This information is provided for two "vintages" of buildings, to account for new construction and retrofits of older buildings.
The second table provides Infiltration assumptions for both systems. The CASE Team is particularly interested in whether the infiltration assumptions are representative for indoor CEH facilities, or if the buildings are righter due to odor control requirements.

## HVAC System
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
HVAC system - Controlled Environment Horticulture
Vintage | Space/Thermal Zone | Heating | Cooling | Air Distribution | Other Systems | Source
Pre 2022 | Horticulture_Vegetative | None | DX (RTU) | CAV | Dehumidifier 2.41L/kWh
| Horticulture_Flowering | Electric Resistance | DX (RTU) | CAV | Dehumidifier 2.41L/kWh
| Processing Area | Furnace (Gas) | DX (RTU) | CAV | Dehumidifier 2.41L/kWh
| Horticulture_Drying | None | DX (RTU) | CAV | Dehumidifier 2.41L/kWh
| Storage and Shipping | Furnace (Gas) | DX (RTU) | CAV | Airside economizers (Integrated) | T24, 2013 CZ12: 75 dry bulb; CZ dependent
| Office | Furnace (Gas) | DX (RTU) | CAV | Airside economizers (Integrated) | T24, 2013 CZ12: 75 dry bulb; CZ dependent
| Restrooms | Furnace (Gas) | DX (RTU) | CAV | Airside economizers (Integrated) | T24, 2013 CZ12: 75 dry bulb; CZ dependent
| Security office | Furnace (Gas) | DX (RTU) | CAV | Airside economizers (Integrated)
2022+ | Horticulture_Vegetative | Heat Pump | DX (RTU) | CAV | Dehumidifier 2.41L/kWh
| Horticulture_Flowering | Recovered Heat | VAV 12.23 EER | VAV | N/A
| Processing Area | Heat Pump | DX (RTU) | CAV | Dehumidifier 2.41L/kWh
| Horticulture_Drying | None | DX (RTU) | CAV | Dehumidifier 2.41L/kWh | Dry rooms typically use standalone dehumidifiers to remove moisture and then trim the temperature.
| Storage and Shipping | Heat Pump | DX (RTU) | CAV | Airside economizers (Integrated)
| Office | Heat Pump | DX (RTU) | CAV | Airside economizers (Integrated)
| Restrooms | Heat Pump | DX (RTU) | CAV | Airside economizers (Integrated) | T24, 2025
| Security office | Heat Pump | DX (RTU) | CAV | Airside economizers (Integrated)
Efficiency of HVAC system (Efficiency is capacity-dependent. The following Table provides a general estimate of system efficiency based on what we saw in the existing prototype runs, or assuming cooling load based on rule of thumb)
Vintage | Upgrade/Installed year | Heating | Cooling | Other Systems | Source | Note
Pre 2022 | 2019 | Thermal Efficiency of 80% | varies |  | Code Readiness report. | All eletctric Electric resistance is the most common supplemental heat source in California For Flower room, see Flower Room HVAC Equipment tab
2022+ | 2025 | Heat Pump | varies |  |  | For Flower room, see Flower Room HVAC Equipment tab
Fan Power
Vintage | Approach | System | Total Static Pressure (TSP) (in w.c.) [PNNL 20405, 2010, Table 5.11] | Fan Efficiency [ACM 2025] | Fan Motor and Drive Efficiency [ACM 2025, Table 13] | W/cfm [ACM 2025, Table 14 and 15] | Data Source or Other Notes
Existing | PNNL TSP | CAV Office | 2.5 (system <7,437 cfm) | 0.65 | ~0.9 (The full-load efficiency of the motor serving the fan- will be determined based on ACM 2025, Table 13) |  | ACM 2025, PNNL 20405, 2010
|  | CAV Storage and Shipping | 2.5 (system <7,437 cfm) | 0.65
|  | CAV Security | 2.5 (system <7,437 cfm) | 0.65
|  | CAV Restrooms | 2.5 (system <7,437 cfm) | 0.65
Brake horse power (bhp)=(Supply cfm*TSP in w.c.)/(6356*Fan efficiency)
Fan power (w/cfm) = bhp/motor and drive efficiency *746
New Construction | ACM 2025 | CAV Office | 3.7083 | 0.65 | 0.9 |  | ACM 2025
|  | CAV Storage and Shipping | 3.7083
New Construction |  | CAV Security | 3.7083
New Construction |  | CAV Restrooms | 3.7083
Circulation Fans are defined on the equipment tab
This tab provides procides assumptions about HVAC equipment, consistent with Title 24, Part 6 Nonresidential requirements. This information is provided for two "vintages" of buildings, to account for new construction and retrofits of older buildings. The New Construction for the flowering room is consistent with the 2028 CEH Space Conditioning proposal.
The first table includes heating and cooling system types and air distribution (constant air volume vs. variable air volume), and standalone dehumidifiers are listed under Other Systems.
The second table addressed the assumed HVAC system efficiency for each table.
The third table addresses fan power.
The CASE Team would appreciate input on the HVAC and fan power assumptions.

## Heating-No area used to convert (hidden)
Small Office Heating System | Only Conversion factors |  |  | Multiplied by Floor area at FZ level |  |  | No. of zones with | [12 empty] | Converting the FZ data to the CZ level by applying total small office floor area in each FZ
| Saturation (Electric) | Saturation (Gas) | Saturation (Other Fuels) | #REF! | #REF! | #REF! | Elec | Gas |  | Forecast Zone | Building-type | End Use | End Use Saturation | Electric Fuel Share | Gas Fuel Share | Other Fuel Share | Saturation (Electric) | Saturation (Gas) | Saturation (Other Fuels) |  | Saturation (Gas) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | 16.95% | 79.95% | 3.1% | #REF! | #REF! | #REF! | 1 | 4 | #REF! | Statewide | Office, Small | Heating | 91.16% | 43.38% | 55.53% | 1.095% | 39.54% | 50.62% | 0.9982% | FZ0 | 72.77% | 13.02% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.307% | 0% | 0% | 0.0009446% | 2.316% | 57.12%
2 | 11.95% | 81.41% | 6.641% | #REF! | #REF! | #REF! | 0 | 5 | #REF! | FCZ1 | Office, Small | Heating | 91.3% | 30.73% | 68.38% | 0.8879% | 28.06% | 62.43% | 0.8107% | FCZ1 | 62.43% | 0% | 0% | 32.74% | 18.97% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 10.72% | 0% | 0% | 0% | 0%
3 | 27.16% | 71.74% | 1.095% | #REF! | #REF! | #REF! | 1 | 4 | #REF! | FCZ2 | Office, Small | Heating | 86.21% | 11.93% | 81.41% | 6.656% | 10.29% | 70.19% | 5.739% | FCZ2 | 70.19% | 9.484% | 56.29% | 4.411% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003885%
4 | 28.94% | 70.4% | 0.6547% | #REF! | #REF! | #REF! | 1 | 4 | #REF! | FCZ3 | Office, Small | Heating | 89.76% | 25.36% | 66.49% | 8.147% | 22.76% | 59.68% | 7.313% | FCZ3 | 59.68% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 50.59% | 0% | 0% | 0% | 0% | 9.088%
5 | 25.62% | 74.18% | 0.1998% | #REF! | #REF! | #REF! | 1 | 4 | #REF! | FCZ4 | Office, Small | Heating | 89.76% | 25.36% | 66.49% | 8.147% | 22.76% | 59.68% | 7.313% | FCZ4 | 59.68% | 0% | 0% | 2.171% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 13.17% | 43.33% | 0% | 0% | 0% | 1.005%
6 | 55.38% | 44.61% | 0.01227% | #REF! | #REF! | #REF! | 3 | 2 | #REF! | FCZ5 | Office, Small | Heating | 92.22% | 20.5% | 78.91% | 0.5904% | 18.9% | 72.77% | 0.5444% | FCZ5 | 72.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.314% | 68.99% | 0% | 0% | 0.4653%
7 | 50.12% | 49.68% | 0.1953% | #REF! | #REF! | #REF! | 2 | 3 | #REF! | FCZ6 | Office, Small | Heating | 92.65% | 25.46% | 74.34% | 0.201% | 23.59% | 68.87% | 0.1862% | FCZ6 | 68.87% | 0% | 0% | 35.99% | 10.6% | 22.27% | 0.008275% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
8 | 59.97% | 40.02% | 0.005247% | #REF! | #REF! | #REF! | 3 | 2 | #REF! | FCZ7 | Office, Small | Heating | 95.23% | 66.15% | 33.85% | 0% | 63% | 32.24% | 0% | FCZ7 | 32.24% | 0% | 0% | 0% | 0% | 0% | 6.089% | 0% | 14.18% | 10.41% | 0% | 0% | 0% | 0% | 1.452% | 0% | 0.1054%
9 | 42.66% | 57.34% | 0% | #REF! | #REF! | #REF! | 3 | 2 | #REF! | FCZ8 | Office, Small | Heating | 93.21% | 54.12% | 45.88% | 0% | 50.45% | 42.76% | 0% | FCZ8 | 42.76% | 0% | 0% | 0% | 0% | 0.07821% | 26.17% | 0% | 0% | 15.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0.6032%
10 | 50.22% | 49.41% | 0.3751% | #REF! | #REF! | #REF! | 2 | 3 | #REF! | FCZ9 | Office, Small | Heating | 94.53% | 5.954% | 91.12% | 2.923% | 5.628% | 86.13% | 2.763% | FCZ9 | 86.13% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 67.6% | 10.42% | 0% | 8.106%
11 | 23.93% | 70.22% | 5.851% | #REF! | #REF! | #REF! | 1 | 4 | #REF! | FCZ10 | Office, Small | Heating | 91.24% | 45.97% | 54.03% | 0% | 41.94% | 49.3% | 0% | FCZ10 | 49.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 35.09% | 0% | 0% | 0% | 11.91% | 0.04718% | 2.243%
12 | 27.03% | 70.96% | 2.019% | #REF! | #REF! | #REF! | 1 | 4 | #REF! | FCZ11 | Office, Small | Heating | 98.09% | 53.51% | 45.77% | 0.7163% | 52.49% | 44.9% | 0.7026% | FCZ11 | 44.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.66% | 0% | 0% | 0% | 0.0001136% | 5.987% | 0.2494%
13 | 13.82% | 84.52% | 1.661% | #REF! | #REF! | #REF! | 1 | 4 | #REF! | FCZ12c | Office, Small | Heating | 90.06% | 57.99% | 41.76% | 0.2504% | 52.22% | 37.61% | 0.2255% | FCZ12 | 44.19% | 0% | 0% | 0% | 0% | 0% | 2.915% | 27.76% | 0.8565% | 0% | 12.32% | 0% | 0% | 0% | 0.2927% | 0.05141% | 0%
14 | 36.37% | 62.75% | 0.8744% | #REF! | #REF! | #REF! | 3 | 2 | #REF! | FCZ12i | Office, Small | Heating | 87.84% | 42.06% | 57.8% | 0.1388% | 36.94% | 50.77% | 0.1219% | FCZ13 | 53.37% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.2246% | 53.15% | 0% | 0% | 0% | 0%
15 | 52.66% | 46.63% | 0.712% | #REF! | #REF! | #REF! | 3 | 2 | #REF! | FCZ13 | Office, Small | Heating | 86.85% | 38.55% | 61.45% | 0% | 33.48% | 53.37% | 0% | FCZ14 | 72.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 72.77% | 0% | 0% | 0% | 0%
16 | 32.94% | 66.07% | 0.9849% | #REF! | #REF! | #REF! | 1 | 4 | #REF! | FCZ16 | Office, Small | Heating | 73.64% | 48.2% | 51.8% | 0% | 35.5% | 38.14% | 0% | FCZ15 | 72.77% | 0% | 0.1411% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.41% | 38.31% | 0% | 0% | 0% | 1.898%
[10 empty] | FCZ17 | Office, Small | Heating | 90.56% | 35.22% | 64.78% | 0% | 31.89% | 58.67% | 0% | FCZ16 | 38.14% | 0% | 0% | 0% | 0% | 0% | 6.553% | 0% | 10.64% | 20.95% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[20 empty] | FCZ17 | 58.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 58.29% | 0% | 0% | 0% | 0% | 0% | 0% | 0.379%
[20 empty] | FCZ18 | 58.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 58.67% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[20 empty] | FCZ19 | 44.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.01087% | 44.88% | 0%
[20 empty] | FCZ20 | 49.3% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 49.3%
[20 empty] | Sum |  | 22.51% | 56.43% | 75.31% | 29.57% | 22.35% | 41.73% | 27.76% | 25.68% | 164.2% | 86.07% | 96.71% | 221.6% | 136.6% | 24.1% | 53.29% | 130.6%
[22 empty] | 79.95% | 81.41% | 71.74% | 70.4% | 74.18% | 44.61% | 49.68% | 40.02% | 57.34% | 49.41% | 70.22% | 70.96% | 84.52% | 62.75% | 46.63% | 66.07%
[21 empty] | Saturation (Electric) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
[20 empty] | FZ0 | 18.9% | 3.383% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.07975% | 0% | 0% | 0.0002454% | 0.6015% | 14.84%
[20 empty] | FCZ1 | 28.06% | 0% | 0% | 14.71% | 8.527% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.82% | 0% | 0% | 0% | 0%
[20 empty] | FCZ2 | 10.29% | 1.39% | 8.249% | 0.6465% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0005692%
[20 empty] | FCZ3 | 22.76% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 19.3% | 0% | 0% | 0% | 0% | 3.467%
[20 empty] | FCZ4 | 22.76% | 0% | 0% | 0.8282% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.025% | 16.53% | 0% | 0% | 0% | 0.3835%
[20 empty] | FCZ5 | 18.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.8609% | 17.92% | 0% | 0% | 0.1209%
[20 empty] | FCZ6 | 23.59% | 0% | 0% | 12.33% | 3.631% | 7.628% | 0.002835% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[20 empty] | FCZ7 | 63% | 0% | 0% | 0% | 0% | 0% | 11.9% | 0% | 27.71% | 20.34% | 0% | 0% | 0% | 0% | 2.839% | 0% | 0.206%
[20 empty] | FCZ8 | 50.45% | 0% | 0% | 0% | 0% | 0.09226% | 30.87% | 0% | 0% | 18.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0.7115%
[20 empty] | FCZ9 | 5.628% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.418% | 0.6811% | 0% | 0.5297%
[20 empty] | FCZ10 | 41.94% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 29.86% | 0% | 0% | 0% | 10.14% | 0.04014% | 1.908%
[20 empty] | FCZ11 | 52.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 45.2% | 0% | 0% | 0% | 0.0001328% | 7% | 0.2916%
[20 empty] | FCZ12 | 44.58% | 0% | 0% | 0% | 0% | 0% | 2.94% | 28% | 0.864% | 0% | 12.43% | 0% | 0% | 0% | 0.2952% | 0.05186% | 0%
[20 empty] | FCZ13 | 33.48% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.1409% | 33.34% | 0% | 0% | 0% | 0%
[20 empty] | FCZ14 | 18.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 18.9% | 0% | 0% | 0% | 0%
[20 empty] | FCZ15 | 18.9% | 0% | 0.03665% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.42% | 9.953% | 0% | 0% | 0% | 0.4929%
[20 empty] | FCZ16 | 35.5% | 0% | 0% | 0% | 0% | 0% | 6.098% | 0% | 9.905% | 19.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[20 empty] | FCZ17 | 31.89% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 31.69% | 0% | 0% | 0% | 0% | 0% | 0% | 0.206%
[20 empty] | FCZ18 | 31.89% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 31.89% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[20 empty] | FCZ19 | 52.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.01271% | 52.48% | 0%
[20 empty] | FCZ20 | 41.94% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 41.94%
[20 empty] | Sum |  | 4.773% | 8.286% | 28.52% | 12.16% | 7.72% | 51.81% | 28% | 38.48% | 122.2% | 87.49% | 32.96% | 84.4% | 22.34% | 13.97% | 60.17% | 65.1%
[20 empty] | Saturation (Elec) at CZ |  | 16.95% | 11.95% | 27.16% | 28.94% | 25.62% | 55.38% | 50.12% | 59.97% | 42.66% | 50.22% | 23.93% | 27.03% | 13.82% | 36.37% | 52.66% | 32.94%
[21 empty] | Saturation (Other Fuels) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
[20 empty] | FZ0 | 0.5444% | 0.09745% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.002297% | 0% | 0% | 7.067e-06% | 0.01733% | 0.4273%
[20 empty] | FCZ1 | 0.8107% | 0% | 0% | 0.4251% | 0.2463% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.1393% | 0% | 0% | 0% | 0%
[20 empty] | FCZ2 | 5.739% | 0.7754% | 4.602% | 0.3607% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0003176%
[20 empty] | FCZ3 | 7.313% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 6.2% | 0% | 0% | 0% | 0% | 1.114%
[20 empty] | FCZ4 | 7.313% | 0% | 0% | 0.2661% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.614% | 5.31% | 0% | 0% | 0% | 0.1232%
[20 empty] | FCZ5 | 0.5444% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0248% | 0.5161% | 0% | 0% | 0.003482%
[20 empty] | FCZ6 | 0.1862% | 0% | 0% | 0.09731% | 0.02866% | 0.06021% | 2.237e-05% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[20 empty] | FCZ7 | 0% | bar: 1 to 16
[20 empty] | FCZ8 | 0% | bar: 1 to 16
[20 empty] | FCZ9 | 2.763% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.169% | 0.3344% | 0% | 0.2601%
[20 empty] | FCZ10 | 0% | bar: 1 to 16
[20 empty] | FCZ11 | 0.7026% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.605% | 0% | 0% | 0% | 1.778e-06% | 0.09369% | 0.003903%
[20 empty] | FCZ12 | 0.1737% | 0% | 0% | 0% | 0% | 0% | 0.01146% | 0.1091% | 0.003367% | 0% | 0.04843% | 0% | 0% | 0% | 0.00115% | 0.0002021% | 0%
[20 empty] | FCZ13 | 0% | bar: 1 to 16
[20 empty] | FCZ14 | 0.5444% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.5444% | 0% | 0% | 0% | 0%
[20 empty] | FCZ15 | 0.5444% | 0% | 0.001056% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.2425% | 0.2867% | 0% | 0% | 0% | 0.0142%
[20 empty] | FCZ16 | 0% | bar: 1 to 16
[20 empty] | FCZ17 | 0% | bar: 1 to 16
[20 empty] | FCZ18 | 0% | bar: 1 to 16
[20 empty] | FCZ19 | 0.7026% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.0001702% | 0.7024% | 0%
[20 empty] | FCZ20 | 0% | bar: 1 to 16
[20 empty] | Sum |  | 0.0087283 | 0.046034 | 0.011491 | 0.00275 | 0.00060208 | 0.00011479 | 0.001091 | 3.3666e-05 | 0 | 0.0065343 | 0.080586 | 0.06305 | 0.02685 | 0.0033575 | 0.0081364 | 0.019462
[20 empty] | Saturation (Elec) at CZ |  | 3.1% | 6.641% | 1.095% | 0.6547% | 0.1998% | 0.01227% | 0.1953% | 0.005247% | 0% | 0.3751% | 5.851% | 2.019% | 1.661% | 0.8744% | 0.712% | 0.9849%
Note on V2: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on W2: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on X2: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on AA2: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on AA28: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.

## Flower Room HVAC Equipment
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
|  |  | Pre-2022 | 2022+ | Notes
Design Day Sizing | RTU Coil | Design Supply Air Temperature [F] | 55 | 50
|  | Design Supply Air Humidity Ratio [-] | 0.008 | 0.0072
| RTU System | Type of Load to Size On | Sensible | Latent
|  | Cooling Supply Air Flow Rate per Unit Cooling Capacity [m3/s/W] | 4.7e-05 | 3.89e-05
|  | Cooling Design Capacity [W] | 130123 | 140674
|  | Cooling Design Capacity [tons] | 37 | 40
|  | Central Cooling Capacity Control Method | VT | VAV
Annual Simulation | Standalone Dehumidifier | Rated Water Removal [L/day] | 2180 | n/a
|  | Rated Energy Factor [L/kWh] | 2.41 | n/a
|  | Rated Air Flow Rate [m3/s] | 5.4 | n/a
|  | Water Removal Curve | See right | n/a
|  | Energy Factor Curve | See right | n/a
|  | Part Load Fraction Correlation Curve | See right | n/a
|  | Min Zone Dry-bulb Temperature for Operation [F] | 50 | n/a | Thermostat controls to 70-82 F
|  | Max Zone Dry-bulb Temperature for Operation [F] | 90 | n/a | Thermostat controls to 70-82 F
|  | Off-Cycle Parasitic Electric Load [W] | 0 | n/a
| RTU Cooling Coil | Compressor Speeds | 1 | 8
|  | Low Speed COP | n/a | 3.233 | Dehumidification mode: low fan & high compressor
|  | Low Speed SHR | n/a | 0.6943
|  | Low Speed Capacity [tons] | n/a | 7.8253
|  | High Speed COP | 3.5 | 3.586 | Sensible mode: high fan & high compressor
|  | High Speed SHR | 0.8 | 0.6703
|  | High Speed Capacity [tons] | 37 | 40 | See more details for AIO speeds on AIO Coil Speeds tab
| RTU Heating Coil | Coil Type | Electric | Hot Gas Reheat
|  | Efficiency | 1 | 0.9 | Max possible heat reclaim effectiveness for AIO when cooling coil operates

## 2022+ Flower Room Coil Speeds
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
All-In-One RTU DX Coil Parameters for each Compressor Speed
Compressor Speed
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Reference Unit Gross Rated Total Cooling Capacity [W] | 18232.4202 | 32405.1613 | 41619.3157 | 54132.2782 | 66107.7248 | 71388.2793 | 81649.2954 | 93197.4795
Reference Unit Gross Rated Total Cooling Capacity [tons] | 5.1843 | 9.2142 | 11.8342 | 15.3922 | 18.7974 | 20.2989 | 23.2166 | 26.5002
Reference Unit Gross Rated Sensible Heat Ratio [-] | 0.6943 | 0.6828 | 0.683 | 0.6961 | 0.6787 | 0.677 | 0.6752 | 0.6703
Reference Unit Gross Rated Cooling COP [-] | 3.2333 | 3.7823 | 3.8355 | 3.7011 | 3.9741 | 3.9371 | 3.8196 | 3.586
Reference Unit Rated Air Flow Rate [m3/s] | 0.8849 | 1.4158 | 1.7698 | 2.3361 | 2.6547 | 2.8317 | 3.1856 | 3.5396
Reference Unit Rated Air Flow Rate [cfm] | 1875 | 3000 | 3750 | 4950 | 5625 | 6000 | 6750 | 7500

## Thermostat
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
Thermostat Setpoints - Controlled Environment Horticulture
Space/Thermal Zone | Setpoint | CZ1 | CZ2 | CZ3 | CZ4 | CZ5 | CZ6 | CZ7 | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Source and Notes
Office | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Cooling Setback (F) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Security | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Restrooms | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Storage and Shipping | Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | Storage is typically cool and dry to preserve product.
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
| Cooling Setback (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Processing | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | T24 2022 - Appendix 5.4B. RH is kept below 50% to avoid rehydrating product during trimming and packaging.
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
| Cooling Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Horticulture_Drying | Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | Drying room is not typically occupied, kept at 60F and 60%RH to dry plants.
| Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Cooling Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Horticulture_Cloning | Heating Setpoint (F) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | ASABE/ASHRAE P653/ 2050 Model Assume no heating
| Heating Setback (F) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Cooling Setpoint (F) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
| Cooling Setback (F) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Horticulture_Vegetative | Heating Setpoint (F) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 2050 Partners Prototype Assume no heating
| Heating Setback (F) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Cooling Setpoint (F) | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
| Cooling Setback (F) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Horticulture_Flowering | Heating Setpoint (F) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | See Latent Load and Setpoint tab.
| Heating Setback (F) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Cooling Setpoint (F) | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable | Variable
| Cooling Setback (F) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
[19 empty] | 82 | 79 | 73
This tab provides thermostat heating and cooling setpointsand setbacks for rooms where these values do not vary with plant grow cycles.
Setpoints depend on lighting type. Older vintages may have non-LED grow lights, while new construction will have LEDs. When using LEDs, setpoints can be higher. This is because leaves heat up from radiant heat and lower temps are needed when leaves get hotter with non-LED lights.
The CASE Team would like input on whether different temperature setpoints should be considered for the older vintage than for new construction.
The setpoints for Office, Security, and Restrooms and have been set based on the Alternative Compliance Manual.
The Statewide CASE Team is especially interested in put on typical setpoints for the other spaces that are specific to CEH facilities.

## Water Heater
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
Water Heater Summary - Controlled Environment Horticulture
Vintage | WH Type | UEF | Tank Volume (gal) | Tank Loss
Existing | Electric | 0.93 | 40 | TBD
New Construction | Electric | 0.93 | 40 | TBD
The Water Heater assumptions are based on the medium office prototype. Load profile will be pulled from ACM.

## Cooking Euipment (hidden)
Forecast Zone | Building-type | End Use |  | End Use Saturation | Electric Fuel Share | Gas Fuel Share | Other Fuel Share | Saturation (Electric) | Saturation (Gas) | Saturation (Other Fuels)
Statewide | Office, Small | Commercial-Grade Cooking Equipment |  | 2.012% | 36.73% | 62.89% | 0.3769% | 0.739% | 1.265% | 0.007583%
FCZ1 | Office, Small | Commercial-Grade Cooking Equipment |  | 1.614% | 47.99% | 50.25% | 1.763% | 0.7743% | 0.8108% | 0.02844%
FCZ2 | Office, Small | Commercial-Grade Cooking Equipment | Gas | 1.47% | 17.58% | 82.42% | 0% | 0.2584% | 1.212% | 0%
FCZ3 | Office, Small | Commercial-Grade Cooking Equipment |  | 2.476% | 76.95% | 23.05% | 0% | 1.905% | 0.5707% | 0%
FCZ4 | Office, Small | Commercial-Grade Cooking Equipment |  | 2.476% | 76.95% | 23.05% | 0% | 1.905% | 0.5707% | 0%
FCZ5 | Office, Small | Commercial-Grade Cooking Equipment |  | 5.007% | 58.14% | 41.86% | 0% | 2.911% | 2.096% | 0%
FCZ6 | Office, Small | Commercial-Grade Cooking Equipment | Gas | 1.688% | 1.713% | 98.29% | 0% | 0.02891% | 1.659% | 0%
FCZ7 | Office, Small | Commercial-Grade Cooking Equipment | Gas | 2.365% | 17.48% | 82.52% | 0% | 0.4135% | 1.952% | 0%
FCZ8 | Office, Small | Commercial-Grade Cooking Equipment |  | 1.616% | 23.25% | 76.75% | 0% | 0.3759% | 1.241% | 0%
FCZ9 | Office, Small | Commercial-Grade Cooking Equipment |  | 2.146% | 24.36% | 75.64% | 0% | 0.5229% | 1.623% | 0%
FCZ10 | Office, Small | Commercial-Grade Cooking Equipment |  | 1.697% | 25.58% | 74.42% | 0% | 0.4339% | 1.263% | 0%
FCZ11 | Office, Small | Commercial-Grade Cooking Equipment |  | 2.092% | 56.74% | 43.26% | 0% | 1.187% | 0.9048% | 0%
FCZ12c | Office, Small | Commercial-Grade Cooking Equipment |  | 2.002% | 37.81% | 62.19% | 0% | 0.7571% | 1.245% | 0%
FCZ12i | Office, Small | Commercial-Grade Cooking Equipment |  | 0.5539% | 75.22% | 24.78% | 0% | 0.4166% | 0.1372% | 0%
FCZ13 | Office, Small | Commercial-Grade Cooking Equipment |  | 1.619% | 48.03% | 51.38% | 0.5852% | 0.7775% | 0.8317% | 0.009472%
FCZ16 | Office, Small | Commercial-Grade Cooking Equipment | Gas | 0.608% | 21.09% | 78.91% | 0% | 0.1282% | 0.4798% | 0%
FCZ17 | Office, Small | Commercial-Grade Cooking Equipment | Gas | 1.033% | 1.761% | 98.24% | 0% | 0.01819% | 1.015% | 0%
Planning Area & Forecast Zone | Building-type | End Use |  | End Use Saturation or Penetration | Electric Fuel Share | Gas Fuel Share | Other Fuel Share | Saturation (Electric) | Saturation (Gas) | Saturation (Other Fuels)
Statewide | Office, Small | Commercial Cooking Space |  | 0.4251% | 36.73% | 62.89% | 0.3769% | 0.1561% | 0.2674% | 0.001602%
FCZ1 | Office, Small | Commercial Cooking Space |  | 0.5597% | 47.99% | 50.25% | 1.763% | 0.2686% | 0.2813% | 0.009865%
FCZ2 | Office, Small | Commercial Cooking Space |  | 0.4216% | 17.58% | 82.42% | 0% | 0.07412% | 0.3475% | 0%
FCZ3 | Office, Small | Commercial Cooking Space |  | 0.2979% | 76.95% | 23.05% | 0% | 0.2292% | 0.06867% | 0%
FCZ4 | Office, Small | Commercial Cooking Space |  | 0.2979% | 76.95% | 23.05% | 0% | 0.2292% | 0.06867% | 0%
FCZ5 | Office, Small | Commercial Cooking Space |  | 0.5818% | 58.14% | 41.86% | 0% | 0.3383% | 0.2435% | 0%
FCZ6 | Office, Small | Commercial Cooking Space |  | 0.3712% | 1.713% | 98.29% | 0% | 0.006357% | 0.3648% | 0%
FCZ7 | Office, Small | Commercial Cooking Space |  | 0.4212% | 17.48% | 82.52% | 0% | 0.07364% | 0.3476% | 0%
FCZ8 | Office, Small | Commercial Cooking Space |  | 0.1957% | 23.25% | 76.75% | 0% | 0.04551% | 0.1502% | 0%
FCZ9 | Office, Small | Commercial Cooking Space |  | 0.2042% | 24.36% | 75.64% | 0% | 0.04975% | 0.1544% | 0%
FCZ10 | Office, Small | Commercial Cooking Space |  | 0.3738% | 25.58% | 74.42% | 0% | 0.0956% | 0.2782% | 0%
FCZ11 | Office, Small | Commercial Cooking Space |  | 0.4803% | 56.74% | 43.26% | 0% | 0.2725% | 0.2078% | 0%
FCZ12c | Office, Small | Commercial Cooking Space |  | 0.5231% | 37.81% | 62.19% | 0% | 0.1978% | 0.3253% | 0%
FCZ12i | Office, Small | Commercial Cooking Space |  | 0.0861% | 75.22% | 24.78% | 0% | 0.06477% | 0.02133% | 0%
FCZ13 | Office, Small | Commercial Cooking Space |  | 0.6377% | 48.03% | 51.38% | 0.5852% | 0.3063% | 0.3277% | 0.003732%
FCZ16 | Office, Small | Commercial Cooking Space |  | 0.1047% | 21.09% | 78.91% | 0% | 0.02207% | 0.0826% | 0%
FCZ17 | Office, Small | Commercial Cooking Space |  | 0.07682% | 1.761% | 98.24% | 0% | 0.001353% | 0.07547% | 0%
Note on I1: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on J1: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on K1: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on I23: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on J23: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on K23: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.

## Air compressor (hidden)
Forecast Zone | Building-type | End Use | End Use Saturation | Electric Fuel Share | Gas Fuel Share | Other Fuel Share | Saturation (Electric) | Saturation (Gas) | Saturation (Other Fuels)
Statewide | Office, Small | Air Compressors | 15.53% | NA | NA | NA | 15.53% | 0% | 0%
FCZ1 | Office, Small | Air Compressors | 16.13% | NA | NA | NA | 16.13% | 0% | 0%
FCZ2 | Office, Small | Air Compressors | 16.05% | NA | NA | NA | 16.05% | 0% | 0%
FCZ3 | Office, Small | Air Compressors | 17.7% | NA | NA | NA | 17.7% | 0% | 0%
FCZ4 | Office, Small | Air Compressors | 17.7% | NA | NA | NA | 17.7% | 0% | 0%
FCZ5 | Office, Small | Air Compressors | 11.29% | NA | NA | NA | 11.29% | 0% | 0%
FCZ6 | Office, Small | Air Compressors | 19.95% | NA | NA | NA | 19.95% | 0% | 0%
FCZ7 | Office, Small | Air Compressors | 11.62% | NA | NA | NA | 11.62% | 0% | 0%
FCZ8 | Office, Small | Air Compressors | 18.25% | NA | NA | NA | 18.25% | 0% | 0%
FCZ9 | Office, Small | Air Compressors | 26.85% | NA | NA | NA | 26.85% | 0% | 0%
FCZ10 | Office, Small | Air Compressors | 8.54% | NA | NA | NA | 8.54% | 0% | 0%
FCZ11 | Office, Small | Air Compressors | 17.53% | NA | NA | NA | 17.53% | 0% | 0%
FCZ12c | Office, Small | Air Compressors | 19.81% | NA | NA | NA | 19.81% | 0% | 0%
FCZ12i | Office, Small | Air Compressors | 15.54% | NA | NA | NA | 15.54% | 0% | 0%
FCZ13 | Office, Small | Air Compressors | 18.42% | NA | NA | NA | 18.42% | 0% | 0%
FCZ16 | Office, Small | Air Compressors | 15.52% | NA | NA | NA | 15.52% | 0% | 0%
FCZ17 | Office, Small | Air Compressors | 24.88% | NA | NA | NA | 24.88% | 0% | 0%
Note on H1: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on I1: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on J1: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.

## Refrigerated (hidden)
Forecast Zone | Building-type | End Use | End Use Saturation | Electric Fuel Share | Gas Fuel Share | Other Fuel Share | Saturation (Electric) | Saturation (Gas) | Saturation (Other Fuels)
Statewide | Office, Small | Commercial-Grade Refrigerators | 84.56% | NA | NA | NA | 84.56% | 0% | 0%
FCZ1 | Office, Small | Commercial-Grade Refrigerators | 79.85% | NA | NA | NA | 79.85% | 0% | 0%
FCZ2 | Office, Small | Commercial-Grade Refrigerators | 86.55% | NA | NA | NA | 86.55% | 0% | 0%
FCZ3 | Office, Small | Commercial-Grade Refrigerators | 82.76% | NA | NA | NA | 82.76% | 0% | 0%
FCZ4 | Office, Small | Commercial-Grade Refrigerators | 82.76% | NA | NA | NA | 82.76% | 0% | 0%
FCZ5 | Office, Small | Commercial-Grade Refrigerators | 85.24% | NA | NA | NA | 85.24% | 0% | 0%
FCZ6 | Office, Small | Commercial-Grade Refrigerators | 83.77% | NA | NA | NA | 83.77% | 0% | 0%
FCZ7 | Office, Small | Commercial-Grade Refrigerators | 82.3% | NA | NA | NA | 82.3% | 0% | 0%
FCZ8 | Office, Small | Commercial-Grade Refrigerators | 88.39% | NA | NA | NA | 88.39% | 0% | 0%
FCZ9 | Office, Small | Commercial-Grade Refrigerators | 100% | NA | NA | NA | 100% | 0% | 0%
FCZ10 | Office, Small | Commercial-Grade Refrigerators | 81.78% | NA | NA | NA | 81.78% | 0% | 0%
FCZ11 | Office, Small | Commercial-Grade Refrigerators | 86.1% | NA | NA | NA | 86.1% | 0% | 0%
FCZ12c | Office, Small | Commercial-Grade Refrigerators | 81.01% | NA | NA | NA | 81.01% | 0% | 0%
FCZ12i | Office, Small | Commercial-Grade Refrigerators | 84.21% | NA | NA | NA | 84.21% | 0% | 0%
FCZ13 | Office, Small | Commercial-Grade Refrigerators | 89.38% | NA | NA | NA | 89.38% | 0% | 0%
FCZ16 | Office, Small | Commercial-Grade Refrigerators | 98.33% | NA | NA | NA | 98.33% | 0% | 0%
FCZ17 | Office, Small | Commercial-Grade Refrigerators | 94.72% | NA | NA | NA | 94.72% | 0% | 0%
Forecast Zone | Building-type | End Use | End Use Saturation | Electric Fuel Share | Gas Fuel Share | Other Fuel Share | Saturation (Electric) | Saturation (Gas) | Saturation (Other Fuels)
Statewide | Office, Small | Commercial-Grade Freezers | 5.974% | NA | NA | NA | 5.974% | 0% | 0%
FCZ1 | Office, Small | Commercial-Grade Freezers | 2.641% | NA | NA | NA | 2.641% | 0% | 0%
FCZ2 | Office, Small | Commercial-Grade Freezers | 3.267% | NA | NA | NA | 3.267% | 0% | 0%
FCZ3 | Office, Small | Commercial-Grade Freezers | 9.272% | NA | NA | NA | 9.272% | 0% | 0%
FCZ4 | Office, Small | Commercial-Grade Freezers | 9.272% | NA | NA | NA | 9.272% | 0% | 0%
FCZ5 | Office, Small | Commercial-Grade Freezers | 12.77% | NA | NA | NA | 12.77% | 0% | 0%
FCZ6 | Office, Small | Commercial-Grade Freezers | 4.874% | NA | NA | NA | 4.874% | 0% | 0%
FCZ7 | Office, Small | Commercial-Grade Freezers | 6.815% | NA | NA | NA | 6.815% | 0% | 0%
FCZ8 | Office, Small | Commercial-Grade Freezers | 7.552% | NA | NA | NA | 7.552% | 0% | 0%
FCZ9 | Office, Small | Commercial-Grade Freezers | 11.15% | NA | NA | NA | 11.15% | 0% | 0%
FCZ10 | Office, Small | Commercial-Grade Freezers | 4.863% | NA | NA | NA | 4.863% | 0% | 0%
FCZ11 | Office, Small | Commercial-Grade Freezers | 4.105% | NA | NA | NA | 4.105% | 0% | 0%
FCZ12c | Office, Small | Commercial-Grade Freezers | 6.665% | NA | NA | NA | 6.665% | 0% | 0%
FCZ12i | Office, Small | Commercial-Grade Freezers | 5.96% | NA | NA | NA | 5.96% | 0% | 0%
FCZ13 | Office, Small | Commercial-Grade Freezers | 4.589% | NA | NA | NA | 4.589% | 0% | 0%
FCZ16 | Office, Small | Commercial-Grade Freezers | 7.967% | NA | NA | NA | 7.967% | 0% | 0%
FCZ17 | Office, Small | Commercial-Grade Freezers | 2.577% | NA | NA | NA | 2.577% | 0% | 0%
Forecast Zone | Building-type | End Use | End Use Saturation | Electric Fuel Share | Gas Fuel Share | Other Fuel Share | Saturation (Electric) | Saturation (Gas) | Saturation (Other Fuels)
Statewide | Office, Small | Frozen Floor Space | 0.03288% | NA | NA | NA | 0.03288% | 0% | 0%
FCZ1 | Office, Small | Frozen Floor Space | 0% | NA | NA | NA | 0% | 0% | 0%
FCZ2 | Office, Small | Frozen Floor Space | 0% | NA | NA | NA | 0% | 0% | 0%
FCZ3 | Office, Small | Frozen Floor Space | 0% | NA | NA | NA | 0% | 0% | 0%
FCZ4 | Office, Small | Frozen Floor Space | 0% | NA | NA | NA | 0% | 0% | 0%
FCZ5 | Office, Small | Frozen Floor Space | 0% | NA | NA | NA | 0% | 0% | 0%
FCZ6 | Office, Small | Frozen Floor Space | 0.4976% | NA | NA | NA | 0.4976% | 0% | 0%
FCZ7 | Office, Small | Frozen Floor Space | 0.01418% | NA | NA | NA | 0.01418% | 0% | 0%
FCZ8 | Office, Small | Frozen Floor Space | 0.1135% | NA | NA | NA | 0.1135% | 0% | 0%
FCZ9 | Office, Small | Frozen Floor Space | 0% | NA | NA | NA | 0% | 0% | 0%
FCZ10 | Office, Small | Frozen Floor Space | 0% | NA | NA | NA | 0% | 0% | 0%
FCZ11 | Office, Small | Frozen Floor Space | 0% | NA | NA | NA | 0% | 0% | 0%
FCZ12c | Office, Small | Frozen Floor Space | 0% | NA | NA | NA | 0% | 0% | 0%
FCZ12i | Office, Small | Frozen Floor Space | 0% | NA | NA | NA | 0% | 0% | 0%
FCZ13 | Office, Small | Frozen Floor Space | 0% | NA | NA | NA | 0% | 0% | 0%
FCZ16 | Office, Small | Frozen Floor Space | 0% | NA | NA | NA | 0% | 0% | 0%
FCZ17 | Office, Small | Frozen Floor Space | 0% | NA | NA | NA | 0% | 0% | 0%
Note on H1: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on I1: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on J1: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on H22: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on I22: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on J22: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on H41: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on I41: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.
Note on J41: Saturation is defined as the % of total floorspace for each combination of end-use and fuel-type.

## Ventilation
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
Outdoor Airflow Rate - Controlled Environment Horticulture
Space/Thermal Zone | Number of People | Floor Area (ft²) | cfm/person [T24, 2025, Equation 120.1-F and Table 120.1-A] | cfm/ft² [T24, 2025, Equation 120.1-F and Table 120.1-A] | Required Exhaust Rate [T24, 2025, Table 120.1-B – minimum exhaust rates] | Total cfm Driven by People | Total cfm Driven by Area | Total cfm Driven by Exhaust | Total cfm | Notes
Horticulture_Vegetative | 0 | 2940 | 0 | 0.18 | 529.2 | 0 | 529.2 | 529.2 | 529.2 | California Building Code 402.3 and Table 402.1 (warehouse)
Horticulture_Flowering | 0 | 12495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | During grow, when CO2 is often enriched, facilities monitor CO2 and ensure that they do not break OSHA limits. These rooms typically are vented at harvest and other times when occupied and not augmented with CO2.
Horticulture_Drying | 0 | 1500 | 0 | 0.18 | 270 | 0 | 270 | 270 | 270
Processing Area | 3 | 2100 | 15 | 0.5 | 1050 | 45 | 1050 | 1050 | 1050 | The processing area is used for plant trimming, typically needs exhaust-driven ventilation at a minimum of 0.5cfm/sf for dust and odor mitigation. This rooms needs a minimum exhaust rate when unoccupied, and it should have a fresh air intake.
Storage | 0 | 2448 | 0 | 0.15 | 367.2 | 0 | 367.2 | 367.2 | 367.2
Office | 15.75 | 3150 | 15 | 0.15 | 472.5 | 236.25 | 472.5 | 472.5 | 472.5 | T24, 2025, Equation 120.1-F and Table 120.1-A
Restrooms | 1 | 420 | 15 | 0.15 | 63 | 15 | 63 | 63 | 63
Security office | 1 | 462 | 15 | 0.15 | 69.3 | 15 | 69.3 | 69.3 | 69.3
This tab provides ventilation rate information.
The Statewide CASE Team is assuming that the flower room will be CO2 enriched and will not have ventilation, and that the processing room (where trimming occurs) will have exhaust-driven ventilation of at least 0.5cfm per square foot for dust and odor mitigation.
The Statewide CASE Team would appreciate input on these assumptions.

## Occupnacy (hidden)
HVAC Operating Hour
Period | Hour | Weekdays Multiplier |  | Saturday | Sunday
12:00 am - 6:00 am | 6 |  | 0
6:00 am -7:00 am | 1 | 20% capcaity | 0.2
7:00 am - 8:00 am | 1 | 70% Capacity | 0.7
8:00 am - 17:00 pm | 9 | Full capacity | 1
17:00 pm - 18:00 pm | 1 | 70% Capacity | 0.7
18:00 pm - 19:00 pm | 1 | 50% capacity | 0.5
19:00 pm - 20:00 pm | 1 | 20% capcaity | 0.3
20:00 pm - 22:00 pm | 2 | 20% capcaity | 0.2
22:00 pm - 12:00 am | 2 |  | 0
|  |  | 11.8 | 3.0267 | 0
Background Data [To be deleted prior to publication]
CEUS 2022 data
Total Weighted Average Annual Operating Hours |  |  | Office, Small | 3286.2707 |  | Working day | 249
Weighted Average Operating Hours Per Day |  |  | Office, Small | 9.0035
Weighted average operating hours per working day (assuming zeo load for weekends) |  |  | Office, Small | 13.1979
Operating Hours Per Day (in 4-hrs bin) By Planning Area & Forecast Zone
Calculation Method | Statewide/ Utility/ FCZ | Building Type | 0< X <=4 | 4< X <=8 | 8< X <=12 | 12< X <=16 | 16< X <=20 | 20<= X <24 | 24 Hrs/Day | Not Available | Total | ← Operating Hours Per Day
Floorspace-Based | Statewide | Office, Small | 0.922% | 37.04% | 52.76% | 5.01% | 1.177% | 0.5665% | 0.6799% | 1.841% | 100%
Annual Operating Hours By Planning Area & Forecast Zone
Calculation Method | Statewide/ Utility/ FCZ | Building Type | <=500 Hrs | 500 < Hrs <=1000 | 1000 < Hrs <=1500 | 1500 < Hrs <=2000 | 2000 < Hrs <=2500 | 2500 < Hrs <=3000 | 3000 < Hrs <=3500 | 3500 < Hrs <=4000 | 4000 < Hrs <=4500 | 4500 < Hrs <=5000 | 5000 < Hrs <=5500 | 5500 < Hrs <=6000 | 6500 < Hrs <=7000 | 7000 < Hrs <=7000 | 7500 < Hrs <=8000 | 8000< Hrs <=8500 | 8001 < Hrs <=8500 | 8500 < Hrs <8760 | 8760 Hours | Total | ← Annual Operating Hours
Floorspace-Based | Statewide | Office, Small | 0.06265% | 0.3069% | 1.574% | 7.177% | 53.64% | 19.27% | 8.738% | 2.484% | 1.993% | 0.6334% | 0.5853% | 0.5399% | 0.2139% | 0.2596% | 0.005075% | 0% | 0.03735% | 0.3457% | 2.132% | 100%
Occupnacy Schedules (existing prototypes extracted from the idf files (presented below)
| PNNL |  |  | DEER |  |  |  |  | CEC
Hour | m2/person | 18.5806 |  |  | Person/m2: 0.0538195521 | 18.5874 |  |  | Person/m2 :0.0538195521 |  | 18.5806
| PNNL (Core+ 3 Perimeter) | PNNL( 1 Perimeter) |  | DEER Normal day | DEER Saturday | DEER (Other day) |  |  | CEC Weekday | CEC Saturday | CEC Sunday
1 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
3 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
6 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
7 | 0.11 | 0.11 |  | 0.1 | 0.1 | 0.05 |  |  | 0.1 | 0.1 | 0.05
8 | 0.21 | 0.21 |  | 0.2 | 0.1 | 0.05 |  |  | 0.2 | 0.1 | 0.05
9 | 1 | 1 |  | 0.95 | 0.3 | 0.05 |  |  | 0.95 | 0.3 | 0.05
10 | 1 | 1 |  | 0.95 | 0.3 | 0.05 |  |  | 0.95 | 0.3 | 0.05
11 | 1 | 0 |  | 0.95 | 0.3 | 0.05 |  |  | 0.95 | 0.3 | 0.05
12 | 1 | 1 |  | 0.95 | 0.3 | 0.05 |  |  | 0.95 | 0.3 | 0.05
13 | 1 | 0 |  | 0.5 | 0.1 | 0.05 |  |  | 0.5 | 0.1 | 0.05
14 | 0.61 | 1 |  | 0.95 | 0.1 | 0.05 |  |  | 0.95 | 0.1 | 0.05
15 | 1 | 0 |  | 0.95 | 0.1 | 0.05 |  |  | 0.95 | 0.1 | 0.05
16 | 1 | 1 |  | 0.95 | 0.1 | 0.05 |  |  | 0.95 | 0.1 | 0.05
17 | 1 | 1 |  | 0.95 | 0.1 | 0.05 |  |  | 0.95 | 0.1 | 0.05
18 | 1 | 0.32 |  | 0.3 | 0.05 | 0.05 |  |  | 0.3 | 0.05 | 0.05
19 | 0.32 | 0.11 |  | 0.1 | 0.05 | 0 |  |  | 0.1 | 0.05 | 0
20 | 0.11 | 0.11 |  | 0.1 | 0 | 0 |  |  | 0.1 | 0 | 0
21 | 0.11 | 0.11 |  | 0.1 | 0 | 0 |  |  | 0.1 | 0 | 0
22 | 0.11 | 0.11 |  | 0.1 | 0 | 0 |  |  | 0.1 | 0 | 0
23 | 0.05 | 0.05 |  | 0.05 | 0 | 0 |  |  | 0.05 | 0 | 0
24 | 0 | 0 |  | 0.05 | 0 | 0 |  |  | 0 | 0 | 0
| 10.63 | 7.13 |  | 9.2 | 2 | 0.6 |  |  | 9.15 | 2 | 0.6
| 10 h entirely occupied | 17 |  | 9 h entirely occupied | 13 | 9 h entirely occupied
DEER 2024 (Old model rebuilt in E+)
DEERSmall Office idf: 07-2024
| Schedule:Compact, |  |  | Schedule:Compact, | [5 empty] | Schedule:Compact, | [5 empty] | Schedule:Compact, | [5 empty] | Schedule:Compact, |  | Schedule:Compact, | Schedule:Compact, | Schedule:Compact, | Schedule:Compact, | Schedule:Compact,
| Hall EL1 Core Spc (G.C5) Occupant Sch, !- Name |  |  | OfficeSmall EL1 North Perim Spc (G.N3) Occupant Sch, !- Name | [5 empty] | OfficeSmall EL1 East Perim Spc (G.E2) Occupant Sch, !- Name | [5 empty] | OfficeSmall EL1 South Perim Spc (G.S1) Occupant Sch, !- Name | [5 empty] | OfficeSmall EL1 West Perim Spc (G.W4) Occupant Sch, !- Name |  | Hall EL1 Core Spc (T.C15) Occupant Sch, !- Name | OfficeSmall EL1 East Perim Spc (T.E12) Occupant Sch, !- Name | OfficeSmall EL1 North Perim Spc (T.N13) Occupant Sch, !- Name | OfficeSmall EL1 South Perim Spc (T.S11) Occupant Sch, !- Name | OfficeSmall EL1 West Perim Spc (T.W14) Occupant Sch, !- Name
| Unit Interval, !- Schedule Type Limits Name |  |  | Unit Interval, !- Schedule Type Limits Name | [5 empty] | Unit Interval, !- Schedule Type Limits Name | [5 empty] | Unit Interval, !- Schedule Type Limits Name | [5 empty] | Unit Interval, !- Schedule Type Limits Name |  | Unit Interval, !- Schedule Type Limits Name | Unit Interval, !- Schedule Type Limits Name | Unit Interval, !- Schedule Type Limits Name | Unit Interval, !- Schedule Type Limits Name | Unit Interval, !- Schedule Type Limits Name
| Through: 12/31, !- Field 1 |  |  | Through: 12/31, !- Field 1 | [5 empty] | Through: 12/31, !- Field 1 | [5 empty] | Through: 12/31, !- Field 1 | [5 empty] | Through: 12/31, !- Field 1 |  | Through: 12/31, !- Field 1 | Through: 12/31, !- Field 1 | Through: 12/31, !- Field 1 | Through: 12/31, !- Field 1 | Through: 12/31, !- Field 1
| For: SummerDesignDay, !- Field 2 |  |  | For: SummerDesignDay, !- Field 2 | [5 empty] | For: SummerDesignDay, !- Field 2 | [5 empty] | For: SummerDesignDay, !- Field 2 | [5 empty] | For: SummerDesignDay, !- Field 2 |  | For: SummerDesignDay, !- Field 2 | For: SummerDesignDay, !- Field 2 | For: SummerDesignDay, !- Field 2 | For: SummerDesignDay, !- Field 2 | For: SummerDesignDay, !- Field 2
| Until: 24:00,1.0, !- Field 3 |  |  | Until: 24:00,1.0, !- Field 3 | [5 empty] | Until: 24:00,1.0, !- Field 3 |  |  | 0 | 0 |  | Until: 24:00,1.0, !- Field 3 | [5 empty] | Until: 24:00,1.0, !- Field 3 |  | Until: 24:00,1.0, !- Field 3 | Until: 24:00,1.0, !- Field 3 | Until: 24:00,1.0, !- Field 3 | Until: 24:00,1.0, !- Field 3 | Until: 24:00,1.0, !- Field 3
| For: WinterDesignDay, !- Field 5 |  |  | For: WinterDesignDay, !- Field 5 | [5 empty] | For: WinterDesignDay, !- Field 5 |  |  | 0 | 0 |  | For: WinterDesignDay, !- Field 5 | [5 empty] | For: WinterDesignDay, !- Field 5 |  | For: WinterDesignDay, !- Field 5 | For: WinterDesignDay, !- Field 5 | For: WinterDesignDay, !- Field 5 | For: WinterDesignDay, !- Field 5 | For: WinterDesignDay, !- Field 5
| Until: 24:00,0.0, !- Field 6 |  |  | Until: 24:00,0.0, !- Field 6 | [5 empty] | Until: 24:00,0.0, !- Field 6 |  |  | 0 | 0 |  | Until: 24:00,0.0, !- Field 6 | [5 empty] | Until: 24:00,0.0, !- Field 6 |  | Until: 24:00,0.0, !- Field 6 | Until: 24:00,0.0, !- Field 6 | Until: 24:00,0.0, !- Field 6 | Until: 24:00,0.0, !- Field 6 | Until: 24:00,0.0, !- Field 6
| For: Weekdays, !- Field 8 |  |  | For: Weekdays, !- Field 8 | [5 empty] | For: Weekdays, !- Field 8 |  |  | 0 | 0 |  | For: Weekdays, !- Field 8 | [5 empty] | For: Weekdays, !- Field 8 |  | For: Weekdays, !- Field 8 | For: Weekdays, !- Field 8 | For: Weekdays, !- Field 8 | For: Weekdays, !- Field 8 | For: Weekdays, !- Field 8
| Until: 06:00,0.0, !- Field 9 |  |  | Until: 06:00,0.0, !- Field 9 | [5 empty] | Until: 06:00,0.0, !- Field 9 |  |  | 0 | 0 |  | Until: 06:00,0.0, !- Field 9 | [5 empty] | Until: 06:00,0.0, !- Field 9 |  | Until: 06:00,0.0, !- Field 9 | Until: 06:00,0.0, !- Field 9 | Until: 06:00,0.0, !- Field 9 | Until: 06:00,0.0, !- Field 9 | Until: 06:00,0.0, !- Field 9
| Until: 07:00,0.10, !- Field 11 |  |  | Until: 07:00,0.10, !- Field 11 | [5 empty] | Until: 07:00,0.10, !- Field 11 |  |  | 0 | 0 |  | Until: 07:00,0.10, !- Field 11 | [5 empty] | Until: 07:00,0.10, !- Field 11 |  | Until: 07:00,0.10, !- Field 11 | Until: 07:00,0.10, !- Field 11 | Until: 07:00,0.10, !- Field 11 | Until: 07:00,0.10, !- Field 11 | Until: 07:00,0.10, !- Field 11
| Until: 08:00,0.20, !- Field 13 |  |  | Until: 08:00,0.20, !- Field 13 | [5 empty] | Until: 08:00,0.20, !- Field 13 |  |  | 0.1 | 0.1 |  | Until: 08:00,0.20, !- Field 13 | [5 empty] | Until: 08:00,0.20, !- Field 13 |  | Until: 08:00,0.20, !- Field 13 | Until: 08:00,0.20, !- Field 13 | Until: 08:00,0.20, !- Field 13 | Until: 08:00,0.20, !- Field 13 | Until: 08:00,0.20, !- Field 13
| Until: 12:00,0.95, !- Field 15 |  |  | Until: 12:00,0.95, !- Field 15 | [5 empty] | Until: 12:00,0.95, !- Field 15 |  |  | 0.2 | 0.1 |  | Until: 12:00,0.95, !- Field 15 | [5 empty] | Until: 12:00,0.95, !- Field 15 |  | Until: 12:00,0.95, !- Field 15 | Until: 12:00,0.95, !- Field 15 | Until: 12:00,0.95, !- Field 15 | Until: 12:00,0.95, !- Field 15 | Until: 12:00,0.95, !- Field 15
| Until: 13:00,0.50, !- Field 17 |  |  | Until: 13:00,0.50, !- Field 17 | [5 empty] | Until: 13:00,0.50, !- Field 17 |  |  | 0.95 | 0.3 |  | Until: 13:00,0.50, !- Field 17 | [5 empty] | Until: 13:00,0.50, !- Field 17 |  | Until: 13:00,0.50, !- Field 17 | Until: 13:00,0.50, !- Field 17 | Until: 13:00,0.50, !- Field 17 | Until: 13:00,0.50, !- Field 17 | Until: 13:00,0.50, !- Field 17
| Until: 17:00,0.95, !- Field 19 |  |  | Until: 17:00,0.95, !- Field 19 | [5 empty] | Until: 17:00,0.95, !- Field 19 |  |  | 0.95 | 0.3 |  | Until: 17:00,0.95, !- Field 19 | [5 empty] | Until: 17:00,0.95, !- Field 19 |  | Until: 17:00,0.95, !- Field 19 | Until: 17:00,0.95, !- Field 19 | Until: 17:00,0.95, !- Field 19 | Until: 17:00,0.95, !- Field 19 | Until: 17:00,0.95, !- Field 19
| Until: 18:00,0.30, !- Field 21 |  |  | Until: 18:00,0.30, !- Field 21 | [5 empty] | Until: 18:00,0.30, !- Field 21 |  |  | 0.95 | 0.3 |  | Until: 18:00,0.30, !- Field 21 | [5 empty] | Until: 18:00,0.30, !- Field 21 |  | Until: 18:00,0.30, !- Field 21 | Until: 18:00,0.30, !- Field 21 | Until: 18:00,0.30, !- Field 21 | Until: 18:00,0.30, !- Field 21 | Until: 18:00,0.30, !- Field 21
| Until: 22:00,0.10, !- Field 23 |  |  | Until: 22:00,0.10, !- Field 23 | [5 empty] | Until: 22:00,0.10, !- Field 23 |  |  | 0.95 | 0.3 |  | Until: 22:00,0.10, !- Field 23 | [5 empty] | Until: 22:00,0.10, !- Field 23 |  | Until: 22:00,0.10, !- Field 23 | Until: 22:00,0.10, !- Field 23 | Until: 22:00,0.10, !- Field 23 | Until: 22:00,0.10, !- Field 23 | Until: 22:00,0.10, !- Field 23
| Until: 24:00,0.05, !- Field 25 |  |  | Until: 24:00,0.05, !- Field 25 | [5 empty] | Until: 24:00,0.05, !- Field 25 |  |  | 0.5 | 0.1 |  | Until: 24:00,0.05, !- Field 25 | [5 empty] | Until: 24:00,0.05, !- Field 25 |  | Until: 24:00,0.05, !- Field 25 | Until: 24:00,0.05, !- Field 25 | Until: 24:00,0.05, !- Field 25 | Until: 24:00,0.05, !- Field 25 | Until: 24:00,0.05, !- Field 25
| For: Saturday, !- Field 27 |  |  | For: Saturday, !- Field 27 | [5 empty] | For: Saturday, !- Field 27 |  |  | 0.95 | 0.1 |  | For: Saturday, !- Field 27 | [5 empty] | For: Saturday, !- Field 27 |  | For: Saturday, !- Field 27 | For: Saturday, !- Field 27 | For: Saturday, !- Field 27 | For: Saturday, !- Field 27 | For: Saturday, !- Field 27
| Until: 06:00,0.0, !- Field 28 |  |  | Until: 06:00,0.0, !- Field 28 | [5 empty] | Until: 06:00,0.0, !- Field 28 |  |  | 0.95 | 0.1 |  | Until: 06:00,0.0, !- Field 28 | [5 empty] | Until: 06:00,0.0, !- Field 28 |  | Until: 06:00,0.0, !- Field 28 | Until: 06:00,0.0, !- Field 28 | Until: 06:00,0.0, !- Field 28 | Until: 06:00,0.0, !- Field 28 | Until: 06:00,0.0, !- Field 28
| Until: 08:00,0.10, !- Field 30 |  |  | Until: 08:00,0.10, !- Field 30 | [5 empty] | Until: 08:00,0.10, !- Field 30 |  |  | 0.95 | 0.1 |  | Until: 08:00,0.10, !- Field 30 | [5 empty] | Until: 08:00,0.10, !- Field 30 |  | Until: 08:00,0.10, !- Field 30 | Until: 08:00,0.10, !- Field 30 | Until: 08:00,0.10, !- Field 30 | Until: 08:00,0.10, !- Field 30 | Until: 08:00,0.10, !- Field 30
| Until: 12:00,0.30, !- Field 32 |  |  | Until: 12:00,0.30, !- Field 32 | [5 empty] | Until: 12:00,0.30, !- Field 32 |  |  | 0.95 | 0.1 |  | Until: 12:00,0.30, !- Field 32 | [5 empty] | Until: 12:00,0.30, !- Field 32 |  | Until: 12:00,0.30, !- Field 32 | Until: 12:00,0.30, !- Field 32 | Until: 12:00,0.30, !- Field 32 | Until: 12:00,0.30, !- Field 32 | Until: 12:00,0.30, !- Field 32
| Until: 17:00,0.10, !- Field 34 |  |  | Until: 17:00,0.10, !- Field 34 | [5 empty] | Until: 17:00,0.10, !- Field 34 |  |  | 0.3 | 0.5 |  | Until: 17:00,0.10, !- Field 34 | [5 empty] | Until: 17:00,0.10, !- Field 34 |  | Until: 17:00,0.10, !- Field 34 | Until: 17:00,0.10, !- Field 34 | Until: 17:00,0.10, !- Field 34 | Until: 17:00,0.10, !- Field 34 | Until: 17:00,0.10, !- Field 34
| Until: 19:00,0.05, !- Field 36 |  |  | Until: 19:00,0.05, !- Field 36 | [5 empty] | Until: 19:00,0.05, !- Field 36 |  |  | 0.1 | 0.5 |  | Until: 19:00,0.05, !- Field 36 | [5 empty] | Until: 19:00,0.05, !- Field 36 |  | Until: 19:00,0.05, !- Field 36 | Until: 19:00,0.05, !- Field 36 | Until: 19:00,0.05, !- Field 36 | Until: 19:00,0.05, !- Field 36 | Until: 19:00,0.05, !- Field 36
| Until: 24:00,0.0, !- Field 38 |  |  | Until: 24:00,0.0, !- Field 38 | [5 empty] | Until: 24:00,0.0, !- Field 38 |  |  | 0.1 | 0 |  | Until: 24:00,0.0, !- Field 38 | [5 empty] | Until: 24:00,0.0, !- Field 38 |  | Until: 24:00,0.0, !- Field 38 | Until: 24:00,0.0, !- Field 38 | Until: 24:00,0.0, !- Field 38 | Until: 24:00,0.0, !- Field 38 | Until: 24:00,0.0, !- Field 38
| For: AllOtherDays, !- Field 40 |  |  | For: AllOtherDays, !- Field 40 | [5 empty] | For: AllOtherDays, !- Field 40 |  |  | 0.1 | 0 |  | For: AllOtherDays, !- Field 40 | [5 empty] | For: AllOtherDays, !- Field 40 |  | For: AllOtherDays, !- Field 40 | For: AllOtherDays, !- Field 40 | For: AllOtherDays, !- Field 40 | For: AllOtherDays, !- Field 40 | For: AllOtherDays, !- Field 40
| Until: 06:00,0.0, !- Field 41 |  |  | Until: 06:00,0.0, !- Field 41 | [5 empty] | Until: 06:00,0.0, !- Field 41 |  |  | 0.1 | 0 |  | Until: 06:00,0.0, !- Field 41 | [5 empty] | Until: 06:00,0.0, !- Field 41 |  | Until: 06:00,0.0, !- Field 41 | Until: 06:00,0.0, !- Field 41 | Until: 06:00,0.0, !- Field 41 | Until: 06:00,0.0, !- Field 41 | Until: 06:00,0.0, !- Field 41
| Until: 18:00,0.05, !- Field 43 |  |  | Until: 18:00,0.05, !- Field 43 | [5 empty] | Until: 18:00,0.05, !- Field 43 |  |  | 0.05 | 0 |  | Until: 18:00,0.05, !- Field 43 | [5 empty] | Until: 18:00,0.05, !- Field 43 |  | Until: 18:00,0.05, !- Field 43 | Until: 18:00,0.05, !- Field 43 | Until: 18:00,0.05, !- Field 43 | Until: 18:00,0.05, !- Field 43 | Until: 18:00,0.05, !- Field 43
| Until: 24:00,0.0; !- Field 45 |  |  | Until: 24:00,0.0; !- Field 45 | [5 empty] | Until: 24:00,0.0; !- Field 45 |  |  | 0.05 | 0 |  | Until: 24:00,0.0; !- Field 45 | [5 empty] | Until: 24:00,0.0; !- Field 45 |  | Until: 24:00,0.0; !- Field 45 | Until: 24:00,0.0; !- Field 45 | Until: 24:00,0.0; !- Field 45 | Until: 24:00,0.0; !- Field 45 | Until: 24:00,0.0; !- Field 45
PNNL 2022
| PNNL Small Office |  |  | Schedule:Compact, |  | For only 1 perimeter zone
| Schedule:Compact, |  |  | BLDG_OCC_SCH_w_SB, !- Name
| BLDG_OCC_SCH_wo_SB, !- Name |  |  | Fraction, !- Schedule Type Limits Name
| Fraction, !- Schedule Type Limits Name |  |  | Through: 12/31, !- Field 1
| Through: 12/31, !- Field 1 |  |  | For: Weekdays, !- Field 2
| For: Weekdays, !- Field 2 |  |  | Until: 01:00,0, !- Field 3
| Until: 01:00,0, !- Field 3 |  |  | Until: 02:00,0, !- Field 5
| Until: 02:00,0, !- Field 5 |  |  | Until: 03:00,0, !- Field 7
| Until: 03:00,0, !- Field 7 |  |  | Until: 04:00,0, !- Field 9
| Until: 04:00,0, !- Field 9 |  |  | Until: 05:00,0, !- Field 11
| Until: 05:00,0, !- Field 11 |  |  | Until: 06:00,0, !- Field 13
| Until: 06:00,0, !- Field 13 |  |  | Until: 07:00,0.11, !- Field 15
| Until: 07:00,0.11, !- Field 15 |  |  | Until: 08:00,0.21, !- Field 17
| Until: 08:00,0.21, !- Field 17 |  |  | Until: 09:00,1, !- Field 19
| Until: 09:00,1, !- Field 19 |  |  | Until: 10:00,1, !- Field 21
| Until: 10:00,1, !- Field 21 |  |  | Until: 11:00,0, !- Field 23
| Until: 11:00,1, !- Field 23 |  |  | Until: 12:00,1, !- Field 25
| Until: 12:00,1, !- Field 25 |  |  | Until: 13:00,0, !- Field 27
| Until: 13:00,0.610394505402463, !- Field 27 |  |  | Until: 14:00,1, !- Field 29
| Until: 14:00,1, !- Field 29 |  |  | Until: 15:00,0, !- Field 31
| Until: 15:00,1, !- Field 31 |  |  | Until: 16:00,1, !- Field 33
| Until: 16:00,1, !- Field 33 |  |  | Until: 17:00,1, !- Field 35
| Until: 17:00,1, !- Field 35 |  |  | Until: 18:00,0.32, !- Field 37
| Until: 18:00,0.32, !- Field 37 |  |  | Until: 19:00,0.11, !- Field 39
| Until: 19:00,0.11, !- Field 39 |  |  | Until: 20:00,0.11, !- Field 41
| Until: 20:00,0.11, !- Field 41 |  |  | Until: 21:00,0.11, !- Field 43
| Until: 21:00,0.11, !- Field 43 |  |  | Until: 22:00,0.11, !- Field 45
| Until: 22:00,0.11, !- Field 45 |  |  | Until: 23:00,0.05, !- Field 47
| Until: 23:00,0.05, !- Field 47 |  |  | Until: 24:00,0, !- Field 49
| Until: 24:00,0, !- Field 49 |  |  | For: Weekends, !- Field 51
| For: Weekends, !- Field 51 |  |  | Until: 01:00,0, !- Field 52
| Until: 01:00,0, !- Field 52 |  |  | Until: 02:00,0, !- Field 54
| Until: 02:00,0, !- Field 54 |  |  | Until: 03:00,0, !- Field 56
| Until: 03:00,0, !- Field 56 |  |  | Until: 04:00,0, !- Field 58
| Until: 04:00,0, !- Field 58 |  |  | Until: 05:00,0, !- Field 60
| Until: 05:00,0, !- Field 60 |  |  | Until: 06:00,0, !- Field 62
| Until: 06:00,0, !- Field 62 |  |  | Until: 07:00,0, !- Field 64
| Until: 07:00,0, !- Field 64 |  |  | Until: 08:00,0, !- Field 66
| Until: 08:00,0, !- Field 66 |  |  | Until: 09:00,0, !- Field 68
| Until: 09:00,0, !- Field 68 |  |  | Until: 10:00,0, !- Field 70
| Until: 10:00,0, !- Field 70 |  |  | Until: 11:00,0, !- Field 72
| Until: 11:00,0, !- Field 72 |  |  | Until: 12:00,0, !- Field 74
| Until: 12:00,0, !- Field 74 |  |  | Until: 13:00,0, !- Field 76
| Until: 13:00,0, !- Field 76 |  |  | Until: 14:00,0, !- Field 78
| Until: 14:00,0, !- Field 78 |  |  | Until: 15:00,0, !- Field 80
| Until: 15:00,0, !- Field 80 |  |  | Until: 16:00,0, !- Field 82
| Until: 16:00,0, !- Field 82 |  |  | Until: 17:00,0, !- Field 84
| Until: 17:00,0, !- Field 84 |  |  | Until: 18:00,0, !- Field 86
| Until: 18:00,0, !- Field 86 |  |  | Until: 19:00,0, !- Field 88
| Until: 19:00,0, !- Field 88 |  |  | Until: 20:00,0, !- Field 90
| Until: 20:00,0, !- Field 90 |  |  | Until: 21:00,0, !- Field 92
| Until: 21:00,0, !- Field 92 |  |  | Until: 22:00,0, !- Field 94 | [6 empty] | Weekday | Saturday | Sunday
| Until: 22:00,0, !- Field 94 |  |  | Until: 23:00,0, !- Field 96 | [5 empty] | Occupancy Load | 13 hours | 2 | 0.6
| Until: 23:00,0, !- Field 96 |  |  | Until: 24:00,0, !- Field 98
| Until: 24:00,0, !- Field 98 |  |  | For: Holiday, !- Field 100
| For: Holiday, !- Field 100 |  |  | Until: 24:00,0.0, !- Field 101
| Until: 24:00,0.0, !- Field 101 |  |  | For: WinterDesignDay, !- Field 103 | [8 empty] | CEUS | [7 empty] | Entirely occupied
| For: WinterDesignDay, !- Field 103 |  |  | Until: 24:00,0.0, !- Field 104 | [8 empty] | Total Weighted Average Annual Operating Hours |  |  |  | Office, Small | 3286.2707 |  | DEER | 10
| Until: 24:00,0.0, !- Field 104 |  |  | For: SummerDesignDay, !- Field 106 | [8 empty] | Weighted Average Operating Hours Per Day |  |  |  | Office, Small | 9.0035 |  | CEC | 9
| For: SummerDesignDay, !- Field 106 |  |  | Until: 24:00,1.0, !- Field 107 | [8 empty] | Weighted average operating hours per working day |  |  |  | Office, Small | 13.1979 |  | PNNL | 9
| Until: 24:00,1.0, !- Field 107 |  |  | For: CustomDay1, !- Field 109
| For: CustomDay1, !- Field 109 |  |  | Until: 24:00,0.0, !- Field 110
| Until: 24:00,0.0, !- Field 110 |  |  | For: CustomDay2, !- Field 112
| For: CustomDay2, !- Field 112 |  |  | Until: 24:00,0.0; !- Field 113
Until: 24:00,0.0; !- Field 113
CBECC 2023
CEC: CBEC 2023
| Schedule:Day:Interval, |  | Schedule:Day:Interval, |  | Schedule:Day:Interval,
| OfficeOccupancyWD, !- Name |  | OfficeOccupancySat, !- Name |  | OfficeOccupancySun, !- Name
| Fraction, !- Schedule Type Limits Name |  | Fraction, !- Schedule Type Limits Name |  | Fraction, !- Schedule Type Limits Name |  |  |  |  | CEC
| No, !- Interpolate to Timestep |  | No, !- Interpolate to Timestep |  | No, !- Interpolate to Timestep
| 01:00, !- Time 1 |  | 01:00, !- Time 1 |  | 01:00, !- Time 1 |  |  |  | 1
| 0, !- Value Until Time 1 |  | 0, !- Value Until Time 1 |  | 0, !- Value Until Time 1 |  |  |  | 2
| 02:00, !- Time 2 |  | 02:00, !- Time 2 |  | 02:00, !- Time 2 |  |  |  | 3
| 0, !- Value Until Time 2 |  | 0, !- Value Until Time 2 |  | 0, !- Value Until Time 2 |  |  |  | 4
| 03:00, !- Time 3 |  | 03:00, !- Time 3 |  | 03:00, !- Time 3 |  |  |  | 5
| 0, !- Value Until Time 3 |  | 0, !- Value Until Time 3 |  | 0, !- Value Until Time 3 |  |  |  | 6
| 04:00, !- Time 4 |  | 04:00, !- Time 4 |  | 04:00, !- Time 4 |  |  |  | 7
| 0, !- Value Until Time 4 |  | 0, !- Value Until Time 4 |  | 0, !- Value Until Time 4 |  |  |  | 8
| 05:00, !- Time 5 |  | 05:00, !- Time 5 |  | 05:00, !- Time 5 |  |  |  | 9
| 0, !- Value Until Time 5 |  | 0, !- Value Until Time 5 |  | 0, !- Value Until Time 5 |  |  |  | 10
| 06:00, !- Time 6 |  | 06:00, !- Time 6 |  | 06:00, !- Time 6 |  |  |  | 11
| 0, !- Value Until Time 6 |  | 0, !- Value Until Time 6 |  | 0, !- Value Until Time 6 |  |  |  | 12
| 07:00, !- Time 7 |  | 07:00, !- Time 7 |  | 07:00, !- Time 7 |  |  |  | 13
| 0.1, !- Value Until Time 7 |  | 0.1, !- Value Until Time 7 |  | 0.05, !- Value Until Time 7 |  |  |  | 14
| 08:00, !- Time 8 |  | 08:00, !- Time 8 |  | 08:00, !- Time 8 |  |  |  | 15
| 0.2, !- Value Until Time 8 |  | 0.1, !- Value Until Time 8 |  | 0.05, !- Value Until Time 8 |  |  |  | 16
| 09:00, !- Time 9 |  | 09:00, !- Time 9 |  | 09:00, !- Time 9 |  |  |  | 17
| 0.95, !- Value Until Time 9 |  | 0.3, !- Value Until Time 9 |  | 0.05, !- Value Until Time 9 |  |  |  | 18
| 10:00, !- Time 10 |  | 10:00, !- Time 10 |  | 10:00, !- Time 10 |  |  |  | 19
| 0.95, !- Value Until Time 10 |  | 0.3, !- Value Until Time 10 |  | 0.05, !- Value Until Time 10 |  |  |  | 20
| 11:00, !- Time 11 |  | 11:00, !- Time 11 |  | 11:00, !- Time 11 |  |  |  | 21
| 0.95, !- Value Until Time 11 |  | 0.3, !- Value Until Time 11 |  | 0.05, !- Value Until Time 11 |  |  |  | 22
| 12:00, !- Time 12 |  | 12:00, !- Time 12 |  | 12:00, !- Time 12 |  |  |  | 23
| 0.95, !- Value Until Time 12 |  | 0.3, !- Value Until Time 12 |  | 0.05, !- Value Until Time 12 |  |  |  | 24
| 13:00, !- Time 13 |  | 13:00, !- Time 13 |  | 13:00, !- Time 13
| 0.5, !- Value Until Time 13 |  | 0.1, !- Value Until Time 13 |  | 0.05, !- Value Until Time 13
| 14:00, !- Time 14 |  | 14:00, !- Time 14 |  | 14:00, !- Time 14
| 0.95, !- Value Until Time 14 |  | 0.1, !- Value Until Time 14 |  | 0.05, !- Value Until Time 14
| 15:00, !- Time 15 |  | 15:00, !- Time 15 |  | 15:00, !- Time 15
| 0.95, !- Value Until Time 15 |  | 0.1, !- Value Until Time 15 |  | 0.05, !- Value Until Time 15
| 16:00, !- Time 16 |  | 16:00, !- Time 16 |  | 16:00, !- Time 16
| 0.95, !- Value Until Time 16 |  | 0.1, !- Value Until Time 16 |  | 0.05, !- Value Until Time 16
| 17:00, !- Time 17 |  | 17:00, !- Time 17 |  | 17:00, !- Time 17
| 0.95, !- Value Until Time 17 |  | 0.1, !- Value Until Time 17 |  | 0.05, !- Value Until Time 17
| 18:00, !- Time 18 |  | 18:00, !- Time 18 |  | 18:00, !- Time 18
| 0.3, !- Value Until Time 18 |  | 0.05, !- Value Until Time 18 |  | 0.05, !- Value Until Time 18
| 19:00, !- Time 19 |  | 19:00, !- Time 19 |  | 19:00, !- Time 19
| 0.1, !- Value Until Time 19 |  | 0.05, !- Value Until Time 19 |  | 0, !- Value Until Time 19
| 20:00, !- Time 20 |  | 20:00, !- Time 20 |  | 20:00, !- Time 20
| 0.1, !- Value Until Time 20 |  | 0, !- Value Until Time 20 |  | 0, !- Value Until Time 20
| 21:00, !- Time 21 |  | 21:00, !- Time 21 |  | 21:00, !- Time 21
| 0.1, !- Value Until Time 21 |  | 0, !- Value Until Time 21 |  | 0, !- Value Until Time 21
| 22:00, !- Time 22 |  | 22:00, !- Time 22 |  | 22:00, !- Time 22
| 0.1, !- Value Until Time 22 |  | 0, !- Value Until Time 22 |  | 0, !- Value Until Time 22
| 23:00, !- Time 23 |  | 23:00, !- Time 23 |  | 23:00, !- Time 23
| 0.05, !- Value Until Time 23 |  | 0, !- Value Until Time 23 |  | 0, !- Value Until Time 23
| 24:00, !- Time 24 |  | 24:00, !- Time 24 |  | 24:00, !- Time 24
| 0.05; !- Value Until Time 24 |  | 0; !- Value Until Time 24 |  | 0; !- Value Until Time 24

## Equipment
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
Equipment - New Construction
Space | Horticulture Lighting (W/ft² canopy) | Gas Power Density (Btu/hr-ft²) | Max Dimming % | Source
Horitculture Vegetative | 24.2354 | 0 | 100 | T24 2025 - Revised CEH Lighting Cannabis Calculations ( lighting power density and dimming on analysis of 6 California facilities provided by Dr. Greenhouse) Note that with LEDs, flower room dimming veries from 60% to 100% over the plant grow cycle.
Horticulture_Flowering | 48.4707 | 0 | 60
Horticulture_Drying | 0 | 0 | 100
Processing Area | 4.4239 | 0 | 100
Storage | 0 | 0 | 100
Office | 0 | 0 | 100
Restrooms | 0 | 0 | 100
Security office | 0 | 0 | 100
Equipment - pre-2022
Space | Horticulture Lighting (W/ft² canopy) | Gas Power Density (Btu/hr-ft²) | Max Dimming % | Source
Horitculture Vegetative | 29.3376 | 0 | 100 | Non-LED, no dimming
Horticulture_Flowering | 44.0063 | 0 | 100
Horticulture_Drying | 0 | 0 | 100
Processing Area | 4.8896 | 0 | 100
Storage | 0 | 0 | 100
Office | 0 | 0 | 100
Restrooms | 0 | 0 | 100
Security office | 0 | 0 | 100
Equipment - all vintages
Space | Circulation Fan (W/ft²) | Gas Power Density (Btu/hr-ft²) | Fan Efficiency | Source
Horitculture Vegetative | 1 | 0 | 0.85 | Need to calculate watts/sq foot of canopy based on number of fans needed to provide 100CFM across canopy, and watts per CFM for each fan.
Horticulture_Flowering | 1 | 0 | 0.85
Horticulture_Drying | 1 | 0 | 0.85
Processing Area | 0 | 0
Storage | 0 | 0
Office | 0 | 0
Restrooms | 0 | 0
Security office | 0 | 0
Space Type | Target PPFD (μmol/m²/s) | Fixture Efficacy (μmol/J) | Column1 | Calculated LPD (W/m²) | Calculated LPD (W/ft²) | Formula (W/m²) | Formula (W/ft²) | Notes
Vegetative Grow Room | 600 | 2.3 |  | 260.8696 | 24.2354 | 260.8696 | 24.2354 | Lower PPFD; blue spectrum; 18 hr photoperiod. 2025 T24 requirements
Flowering Grow Room | 1200 | 2.3 |  | 521.7391 | 48.4707 | 521.7391 | 48.4707 | High PPFD; red spectrum; 12 hr photoperiod. 2025 T24 requirements
Mother/Clone Room | 200 | 2.3 |  | 86.9565 | 8.0785 | 86.9565 | 8.0785 | Gentle lighting for propagation / 24 hr photoperiod. 2025 T24 requirements
Drying/Curing Room | 100 | 2.1 |  | 47.619 | 4.4239 | 47.619 | 4.4239 | Low light; inspection and handling. ASHRAE 189.1 add t
Vegetative Grow Room | 600 | 1.9 |  | 315.7895 | 29.3376 | 315.7895 | 29.3376
Flowering Grow Room | 900 | 1.9 |  | 473.6842 | 44.0063 | 473.6842 | 44.0063
Mother/Clone Room | 200 | 1.9 |  | 105.2632 | 9.7792 | 105.2632 | 9.7792
Drying/Curing Room | 100 | 1.9 |  | 52.6316 | 4.8896 | 52.6316 | 4.8896
This tab provides information on Horticultural Lighting and Circulation Fans in horticultural spaces (not ventilation fans). The Horticultural Lighting schedules are provided in the Schedules tab.
This tab can also include other process loads. The Statewide CASE Team would appreciate input on whether other process loads are significant enough to include here. (Plant-driven latent loads are included in the Latent Load and Setpoint tab)

## Schedules
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
Schedules - Controlled Environment Horticulture
Schedule | Source | Zone | Day | Hour
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Office Areas Occupancy | T24 2022 - Appendix 5.4B Office …......... | Office Restroom Security | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
|  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Office Areas Lighting | T24 2022 - Appendix 5.4B Office …......... | Office Restroom Security | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
|  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office Areas HVAC Availability | T24 2022 - Appendix 5.4B Office …......... | Office Restroom Security | Weekday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Areas Infiltration | T24 2022 - Appendix 5.4B Office …......... | Office Restroom Security | Weekday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Saturday | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
Sunday | bar: Hour 1 to Hour 24
Storage and Processing Areas Occupancy | T24 2022 - Appendix 5.4B Warehouse …......... | Processing Area Storage and Shipping | Weekday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sunday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Storage and Processing Areas Lighting | T24 2022 - Appendix 5.4B Warehouse …......... | Processing Area Storage and Shipping | Weekday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.25 | 0.45 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.3 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.24 | 0.24 | 0.24 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  | Sunday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Horticulture Drying Area Occupancy | T24 2022 - Appendix 5.4B Warehouse …......... | Processing Area Storage and Shipping | Daily | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Horticulture Drying Area Lighting | T24 2022 - Appendix 5.4B Warehouse Typically no lights in Drying arrea | Horticultural Drying | Daily | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.25 | 0.45 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.3 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Horticulture Vegetative Horticultural Lighting | T24 2025 Revised CEH Lighting Calcs | Horticulture_Vegetative | Daily | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Horticulture Vegetative Occupancy | T24 2025 App 5.4 B Light Manufacturing as a place holder | Horticulture_Vegetative | Daily | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
Horticulture Flowering Occupancy | T24 2025 App 5.4 B Light Manufacturing as a place holder | Horticulture_Flowering | Daily | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
Horticulture Flowering Horticultural Lighting - Dimming schedule | T24 2025 Revised CEH Lighting Calcs | Horticulture_Flowering | Initial Stage (7 days) | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Early Stage (7 days) | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Mid Stage (35 days) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Late Stage (14 days) | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Crop Rotation (4 days) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Horticulture Flowering HVAC Availability | HVAC can operate 24/7 as needed | Horticulture_Flowering | Daily | bar: Hour 1 to Hour 24
Horticulture Vegetative HVAC Availability | HVAC can operate 24/7 as needed | Horticulture_Vegetative | Daily | bar: Hour 1 to Hour 24
Horticulture Vegetative Infiltration | Due to 365 operating schedule infiltration is constant | Horticulture_Vegetative | Daily | bar: Hour 1 to Hour 24
Horticulture Flowering Infiltration | Due to 365 operating schedule infiltration is constant | Horticulture_Flowering | Daily | bar: Hour 1 to Hour 24
;
This tab provides schedule assumptions for occupancy, lighting, HVAC availability, and infiltration. All values are provided as a fraction of the total, with a value of 1 being at maximum occupancy, or not dimmed. The Horticulture_Flowering lighting schedule is provided based on the weeks of the grow cycle to reflect common practice.
The Statewide CASE Team would appreciate input on these assumptions.

## Latent Load and Setpoint
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
Schedules - Controlled Environment Horticulture
Schedule | Source | Zone | Day | Hour
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Horticutlure Flowering CEH Transpiration Schedule (% of peak latent load) | Code Readiness Field data (condensate measurement) | Horticulture_Flowering | Initial Stage (7 days) | 12 | 12 | 12 | 12 | 12 | 12 | 30 | 40 | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 35 | 25 | 20 | 18 | 16 | 14
|  |  | Early Stage (7 days) | 14 | 14 | 14 | 14 | 14 | 14 | 60 | 70 | 75 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 60 | 43 | 34 | 26 | 22 | 18
|  |  | Mid Stage (35 days) | 18 | 18 | 18 | 18 | 18 | 18 | 73 | 82 | 91 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 75 | 54 | 41 | 31 | 26 | 21
|  |  | Late Stage (14 days) | 25 | 25 | 25 | 25 | 25 | 25 | 68 | 75 | 83 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 55 | 40 | 35 | 30 | 28
|  |  | Crop Rotation (4 days) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Horticutlure Flowering CEH Setpoint Schedule (Cooling, °F) | Code Readiness Field data, SME data from multiple facilities | Horticulture_Flowering | Initial & Early Stages (14 days) | 79 | 79 | 79 | 79 | 79 | 79 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 79 | 79 | 79 | 79 | 79 | 79
|  |  | Mid Stage (35 days) | 75 | 75 | 75 | 75 | 75 | 75 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 75 | 75 | 75 | 75 | 75 | 75
|  |  | Late Stage (14 days) | 70 | 70 | 70 | 70 | 70 | 70 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 70 | 70 | 70 | 70 | 70 | 70
|  |  | Crop Rotation (4 days) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Horticutlure Flowering CEH Setpoint Schedule (Dehumidifying, %RH) | Code Readiness Field data, SME data from multiple facilities | Horticulture_Flowering | Initial & Early Stages (14 days) | 65 | 65 | 65 | 65 | 65 | 65 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 65 | 65 | 65 | 65 | 65 | 65
|  |  | Mid Stage (35 days) | 54 | 54 | 54 | 54 | 54 | 54 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 54 | 54 | 54 | 54 | 54 | 54
|  |  | Late Stage (14 days) | 46 | 46 | 46 | 46 | 46 | 46 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 46 | 46 | 46 | 46 | 46 | 46
|  |  | Crop Rotation (4 days) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Horticutlure Vegitative CEH Transpiration Schedule (% of peak latent load) | Code Readiness Field data, KEM data from multiple facilities | Horticulture_Vegetative | 365 days | 75 | 54 | 41 | 31 | 26 | 21 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Horticutlure Vegitative CEH Setpoint Schedule (Cooling, °F) | KEM average 8 facilities | Horticulture_Vegetative | 365 days | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
Horticutlure Vegitative CEH Setpoint Schedule (Dehumidifying, %RH) | KEM average 8 facilities | Horticulture_Vegetative | 365 days | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
Horticutlure Drying Latent Load Schedule (% of peak latent load) |  | Horticulture_Drying | 365 days | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Horticutlure Drying Setpoint Schedule (Cooling, °F) |  | Horticulture_Drying | 365 days | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Horticutlure Drying Setpoint Schedule (Dehumidifying, %RH) |  | Horticulture_Drying | 365 days | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Maximum Evapotranspiration Latent Cooling load (Btuh/sq ft) | Max Evaporative Sensible Cooling Load (Btuh/sqft) | Notes
Horticulture Flowering | 80 | 80 | Dr. Greenhouse analysis of latent load for single level facilities gave 70Btuh/sf room area for single level only; 73.8 for single level CA-only, 91 for single and double-level, 118.6 for LED-only (single plus double-level).
Horticulture Vegitative | 105 | 105 | Given the size of these rooms, need to assume double-stack for veg room to serve flower rooms of this size. (Veg canopy = 1/3 total flower canopy.)
Horticulture Drying | 18.4 | 18.4 | This is 600 pints per day, which is 27,600Btuh, which is 18.4Btuh/sqft
;
Note on A7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note that evaporative cooling (sensible bTuh) is equal to latent load for all hours. Model needs to account for both the latent load added by plant transpiration and the sensible cooling from evapotranspiration at the same rate.
This tab provides schedule assumptions for latent loads (% of maximum), temperature setpoints (Farenheit), and humidity setpoints (%RH). For the CEH flower room, this information is provided by specific weeks within the 9-week grow cycle. The vegetative, clone, and drying rooms are assumed to operate the same 365 days per year. The yellow coloring indicates periods when lights are on for the growing rooms. The latent load schedules are based on measured values from the Code Readiness study, and the schedule data is based on input from CEH SMEs.
The table below provides assumptions on the maximum latent load by room.
The Statewide CASE Team would like input on both the schedules and maximum latent loads.

## Energy Usage
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
Energy Consumption - Controlled Environment Horticulture
Prototype | CZ | Total Floorspace (Thousand of ft²) | Electric Energy Intensity (kWh/ft²) | Annual Gas Intensity (kWh/ft²)
| 1 | 36168.6298 | 252 | 0
| 2 | 27133.5821 |  | 0
| 3 | 129904 |  | 0
| 4 | 34408.8832 |  | 0
| 5 | 196250.2784 |  | 0
| 6 | 255059.9168 |  | 0
| 7 | 26496.2355 |  | 0
| 8 | 22940.2074 |  | 0
| 9 | 44442.3296 |  | 0
| 10 | 145476.8768 |  | 0
| 11 | 123786.0736 |  | 0
| 12 | 173680.9856 |  | 0
| 13 | 149542.5408 |  | 0
| 14 | 13661.7203 |  | 0
| 15 | 25627.1962 |  | 0
| 16 | 6700.5734 |  | 0
The Electric Energy Intensity was based on California Department of Cannabis Control ELectricity Supplied by license type, and the average canopy square footage by license type.

## Weights
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
% of Floor Area per CZ and Vintage Bin - Controlled Environment Horticulture |  |  |  | % of Floor Area per CZ and Vintage Bin - Controlled Environment Horticulture
Prototype | CZ | Vintage Bin |  | Prototype | Vintage Bin | CZ
|  | Existing | New Construction |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
CEH | 1 | 88.29% | 11.71% | CEH | Exisiting | 88.29% | 85.5% | 89.12% | 96.42% | 96.9% | 96.97% | 99.86% | 96.94% | 98.4% | 92.85% | 89.25% | 93.69% | 98.35% | 97.75% | 93.07% | 98.05%
| 2 | 85.5% | 14.5% |  | New Construction | 11.71% | 14.5% | 10.88% | 3.585% | 3.095% | 3.025% | 0.1364% | 3.063% | 1.604% | 7.152% | 10.75% | 6.31% | 1.653% | 2.253% | 6.928% | 1.946%
| 3 | 89.12% | 10.88%
| 4 | 96.42% | 3.585%
| 5 | 96.9% | 3.095%
| 6 | 96.97% | 3.025%
| 7 | 99.86% | 0.1364%
| 8 | 96.94% | 3.063%
| 9 | 98.4% | 1.604%
| 10 | 92.85% | 7.152%
| 11 | 89.25% | 10.75%
| 12 | 93.69% | 6.31%
| 13 | 98.35% | 1.653%
| 14 | 97.75% | 2.253%
| 15 | 93.07% | 6.928%
| 16 | 98.05% | 1.946%
Statewide
Ref: CEC 2026 Construction Forecast. 2025 CEH CASE Report
2026 Consturction forecast (millions of square feet)
Background Data [To be deleted prior to publication]
Prototype | CZ | Vintage Bin
|  | Existing | NC
| 1 | 0.6988 | 0.09265
| 2 | 0.4569 | 0.07749
| 3 | 2.62 | 0.3197
| 4 | 1.072 | 0.03986
| 5 | 6.327 | 0.2021
| 6 | 8.264 | 0.2578
| 7 | 1.072 | 0.001464
| 8 | 0.7413 | 0.02342
| 9 | 1.599 | 0.02606
| 10 | 3.609 | 0.278
| 11 | 2.513 | 0.3027
| 12 | 4.533 | 0.3053
| 13 | 5.36 | 0.09011
| 14 | 0.4681 | 0.01079
| 15 | 0.6443 | 0.04796
| 16 | 0.2349 | 0.004662
| Statewide | 40.2133 | 2.0801
Note on G4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: What is the difference between this table and the table range a2:d21? Reply: I was following the template. There’s not a difference in the case of this prototype. It’s a transposed duplicate
There is no California End-Use Survey (CEUS) or similar data for CEH. The Statewide CASE Team used the CEC 2026 Construction forecast and multiplied by 32% based on the assumption of the percentage of CEH squarefootage that is indoor in the 2025 CEH CASE Report
The Statewide CASE Team would welcome data on growth rates and construction rates of indoor CEH by crop type.

## EV Charger
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
EV Charger - Controlled Environment Horticulture
N/A

## Interior Lights
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
Interior Lighting - Controlled Environment Horticulture
Space | New Construction |  |  | Existing
| LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source | LPD (W/ft²) | Additional LPD for Portable Lighting (W/ft²) | Source
Horticulture_Vegetative | 0.4 | - |  | 0.5 | -
Horticulture_Flowering | 0.4 | - |  | 0.5 | -
Processing Area | 0.6 | - |  | 0.75 | -
Storage | 0.4 | - |  | 0.6 | -
Office | 0.6 | 0.2 |  | 0.75 | -
Restrooms | 0.65 | - |  | 0.75 | -
Security office | 0.6 | - |  | 0.75 | -
This tab provides information on task lighting, not horticultural lighting.
The hortiultural lighting is represented in the Equipment tab.

## Ext Lighting
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
Exterior Lighting - Controlled Environment Horticulture
Motion Controlled Luminaires (W) | Non-motion Controlled Luminaires (W) | Total (W) | Source
752 | 726.62 | 1478.62 | T24, 2022. Warehouse Prototype
Exterior Lighting
Items (Assume LZ2) | Assumptions [2019 Outdoor Lighting CASE Report & PNNL 90.1-2010 TSD] |  | Unit | Lighting Power Allowance [T24, 2025, Table 140.7-A & 140.7-B] | Unit | Exterior Lighting Power (W)
IWA (Initial Wattage Allowance) | TBD (Exterior wattage may have additional allotment for security based on jurisidiction) |  |  | 200 | (W) | 200
Parking area | 400 ft² for every parking space Motion control 1 parking space per 830 ft² of gross building area | 12296.3855 | (ft²) | 0.019 | (W/ft²) | 233.6313
Building Entrance | 5 building entrance (1 per 10,000 ft² footprint) | 5 | (count) | 15 | (W/ea) | 75
Building façade | ….... Façade Area = Perimeter × 0.5 × Min (building height in ft and 30 ft) The 0.5 factor assumes that only half of the perimeter walls are lit. -Formula ia developed based on the 2019 Outdoor Lighting CASE report | 4516.2 | (ft²) | 0.1 | (W/ft²) | 451.62
Motion controlled Luminaires | [5 empty] | 233.6313
Non-motion-controlled Luminaires | [5 empty] | 726.62
TOTAL
*Developed based on 2019 Outdoor Lighting CASE Report
Perimeter (ft) | 501.8
Total floor area (ft²) | 25515
Floors | 1
Height (ft) | 18
Background Data [To be deleted prior to publication]
T24, part6, 2025, 130.2(c)3
Title 24, 2025
Exterior lighting assumptions are based on the Conditioned Warehouse Prototype

## PV
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
PV - Controlled Environment Horticulture
N/A
Photovoltaic systems are not required for CEH facilities by the California Energy Code, Title 24, Part 6.

## Notes
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
Data Sources
Prototype | No official prior prototypes. The Statewide CASE Team developed the prototype based on collected data and input from CEH SMEs including Dr. Greenhouse, Kelley Energy Management, J2M Consulting, Zartarian Engineering, and Gillie Consulting.
Codes | Title 24, part 6, referred to as T24(2019, 2022, 2025)
ASHRAE 90.1 (2022)
Others | ACM
| Title 24, 2022 & 2025 - Appendix 5.4A and Appendix 5.4B | https://www.energy.ca.gov/publications/2022/2022-nonresidential-and-multifamily-alternative-calculation-method-reference
| Air leakage Memo, NORESCO, 2025 | https://2050partners.sharepoint.com/:w:/r/sites/CalBEMCollaborativeEfforts/_layouts/15/Doc.aspx?sourcedoc=%7B3BEF8F74-7FAC-44F2-A70C-D76617660066%7D&file=Infiltration_rate_report_14May2025-Short-Version.docx&action=default&mobileredirect=true
| ANSI ASABE EP653 | https://energysolutionsonline.sharepoint.com/:x:/r/teams/extranet/2028-t24/NR%20Library/Covered%20Process/CEH%20Lighting%20Controls/Previous%20Cycle%20Analysis%20(2025)/Reconciliation%20Files%20%26%20Analysis/Warehouse%20-%20ALL%20Plants/JS%20UPDATED__2.25.25__CEH%20Indoor%20Lighting.xlsx?d=wc4895b5252894213a93c70344b0c161f&csf=1&web=1&e=St4i1R
2025 T24 Reviesed CEH Lighting PPE Calcs
| Code Readiness report: Controlled Environment Horticulture: Energy Consumption and Environmental Control Field Study CR22PGE0101-1 | https://etcc-ca.com/reports/market-characterization-indoor-cannabis-cultivation
Market Characterization of Indoor Cannabis Cultivation
Airside Economizers – The Opportunity-Cost of Using Outside Air for Air Conditioning
| A Beginner’s Guide to Proper Ventilation for Cannabis Grow Rooms for OSA numbers | https://www.greenavengerseeds.com/ventilation-for-cannabis-grow/
Data Sets
Dataset | CEC 2026 Construction Forecast
Data set | For existing the Department of Cannabis Control Licensing Data
Notes
Notes | Horticultural lighting and other related equipment EUI is represented in the Equipment sheet of this scorecard. The schedule for horticultural lighting is represented in the schedules tab. Latent load schedules represent water transpired by and evaporative cooling from plants in the space.
Year
1967
1968
1969
1970
1971
1972
1973
1974
1975
1976
1977
1978
1979
1980
1981
1982
1983
1984
1985
1986
1987
1988
1989
1990
1991
1992
1993
1994
1995
1996
1997
1998
1999
2000
2001
2002
2003
2004
2005
2006
2007
2008
2009
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
2020
2021
2022
2023

## FZ-CZ (hidden)
Table B: To be used for converting from New Forecast Zones to Standards Zone (Using 2010 Census Population Data)
Source:CECCFM/Weather/ClimateZoneAnalysis 12-06-16.xlsx
New Forecast Zones
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
1 | 17.9% | 0% | 13.51% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2 | 0% | 0% | 80.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.1939% | 0% | 0% | 0% | 0% | 0%
3 | 0% | 52.43% | 6.285% | 0% | 3.638% | 0% | 52.26% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
4 | 0% | 30.39% | 0% | 0% | 0% | 0% | 15.39% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
5 | 0% | 0% | 0% | 0% | 0% | 0% | 32.33% | 0% | 0.1829% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
6 | 0% | 0% | 0% | 0% | 0% | 0% | 0.01202% | 18.89% | 61.19% | 0% | 0% | 0% | 6.596% | 0% | 0% | 0% | 17.18% | 0% | 0% | 0% | 0%
7 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 62.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
8 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 43.99% | 0% | 0% | 0% | 0% | 1.938% | 0% | 0% | 0% | 27.9% | 0% | 0% | 0% | 0%
9 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 32.29% | 37.22% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 54.92% | 99.35% | 100% | 0% | 0%
10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 71.19% | 86.11% | 27.88% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
11 | 0.4219% | 0% | 0% | 84.77% | 22.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4209% | 0% | 44.55% | 0% | 0% | 0% | 0% | 0%
12 | 0% | 17.18% | 0% | 0% | 72.61% | 4.555% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 99.58% | 100% | 52.65% | 0% | 0% | 0% | 0% | 0%
13 | 0% | 0% | 0% | 0% | 0% | 94.81% | 0% | 0% | 0% | 78.49% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
14 | 0.001298% | 0% | 0% | 0% | 0% | 0% | 0% | 4.506% | 0% | 12.1% | 24.17% | 0.000253% | 0.6623% | 0% | 0% | 0% | 0% | 0% | 0% | 0.02422% | 0%
15 | 3.182% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.09572% | 13.33% | 0.1163% | 0% | 0% | 0% | 0% | 0% | 0% | 99.98% | 0%
16 | 78.5% | 0% | 0.005534% | 15.23% | 1.685% | 0.6395% | 0% | 0.327% | 1.41% | 9.411% | 4.549% | 0.5555% | 0% | 0% | 0% | 2.608% | 0% | 0.6459% | 0% | 0% | 100%
Total | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Ref: | \\carcgl.com\amer\NOR\Prj_SUS\2023\S23668 SCE CA Prototypes Development\Technical\NR\FCZ to CZ.xlsx
33% of CZ 9 comes from FZ 7 and when we apply floor area then this 33% play a very important role.
Small office Floor area (Ref: CEUS 2018 Appendix K)* | [6 empty] | Trasposed Table B: To be used for converting from New Forecast Zones to Standards Zone (Using 2010 Census Population Data)
| Floor Stock (kft2) |  |  | Floor area kft2 |  | FZ/CZ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
FCZ1 | 119595.5776 |  | FZ0 | 43153.1055 | 4.578% | 0 | 17.9% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4219% | 0% | 0% | 0.001298% | 3.182% | 78.5% | 100%
FCZ2 | 33616.997 |  | FCZ1 | 119595.5776 | 12.69% | 1 | 0% | 0% | 52.43% | 30.39% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 17.18% | 0% | 0% | 0% | 0% | 100%
FCZ3 | 9405.1639 |  | FCZ2 | 33616.997 | 3.567% | 2 | 13.51% | 80.2% | 6.285% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.005534% | 100%
FCZ4 | 45237.8174 |  | FCZ3 | 9405.1639 | 0.9978% | 3 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 84.77% | 0% | 0% | 0% | 0% | 15.23% | 100%
FCZ5 | 43153.1055 |  | FCZ4 | 45237.8174 | 4.799% | 4 | 0% | 0% | 3.638% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 22.07% | 72.61% | 0% | 0% | 0% | 1.685% | 100%
FCZ6 | 34954.825 |  | FCZ5 | 43153.1055 | 4.578% | 5 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.555% | 94.81% | 0% | 0% | 0.6395% | 100%
FCZ7 | 168128.0774 |  | FCZ6 | 34954.825 | 3.708% | 6 | 0% | 0% | 52.26% | 15.39% | 32.33% | 0.01202% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100%
FCZ8 | 24229.8711 |  | FCZ7 | 168128.0774 | 17.84% | 7 | 0% | 0% | 0% | 0% | 0% | 18.89% | 0% | 43.99% | 32.29% | 0% | 0% | 0% | 0% | 4.506% | 0% | 0.327% | 100%
FCZ9 | 11692.4715 |  | FCZ8 | 24229.8711 | 2.571% | 8 | 0% | 0% | 0% | 0% | 0.1829% | 61.19% | 0% | 0% | 37.22% | 0% | 0% | 0% | 0% | 0% | 0% | 1.41% | 100%
FCZ10 | 33664.068 |  | FCZ9 | 11692.4715 | 1.24% | 9 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 78.49% | 12.1% | 0% | 9.411% | 100%
FCZ11 | 35588.1912 |  | FCZ10 | 33664.068 | 3.572% | 10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 71.19% | 0% | 0% | 0% | 24.17% | 0.09572% | 4.549% | 100%
FCZ12c | 66439.5525 |  | FCZ11 | 35588.1912 | 3.776% | 11 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 86.11% | 0% | 0% | 0% | 0.000253% | 13.33% | 0.5555% | 100%
FCZ12i | 21127.5797 |  | FCZ12 | 87567.1322 | 9.29% | 12 | 0% | 0% | 0% | 0% | 0% | 6.596% | 62.81% | 1.938% | 0% | 27.88% | 0% | 0% | 0% | 0.6623% | 0.1163% | 0% | 100%
FCZ13 | 29100.3243 |  | FCZ13 | 29100.3243 | 3.087% | 13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.4209% | 99.58% | 0% | 0% | 0% | 0% | 100%
FCZ16 | 38649.9531 |  | FCZ14 | 43153.1055 | 4.578% | 14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 100%
FCZ17 | 14637.0677 |  | FCZ15 | 43153.1055 | 4.578% | 15 | 0% | 0.1939% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 44.55% | 52.65% | 0% | 0% | 0% | 2.608% | 100%
|  |  | FCZ16 | 38649.9531 | 4.1% | 16 | 0% | 0% | 0% | 0% | 0% | 17.18% | 0% | 27.9% | 54.92% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100%
* Small office in CEUS 2018 is any office below 30KSF. It is pretty close to our definition for small office ( any office below 25KSF) |  |  | FCZ17 | 14637.0677 | 1.553% | 17 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 99.35% | 0% | 0% | 0% | 0% | 0% | 0% | 0.6459% | 100%
|  |  | FCZ18 | 14637.0677 | 1.553% | 18 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100%
|  |  | FCZ19 | 35588.1912 | 3.776% | 19 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.02422% | 99.98% | 0% | 100%
|  |  | FCZ20 | 33664.068 | 3.572% | 20 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100%