## README
THIS DRAFT DOCUMENT WAS DEVELOPED BY THE STATEWIDE UTILITY CODES AND STANDARDS ENHANCEMENT (CASE) TEAM
The California Statewide Codes and Standards Enhancement (CASE) Program is funded in part by California utility customers under the auspices of the California Public Utilities Commission. Copyright 2025 Pacific Gas and Electric Company, Southern California Edison, San Diego Gas & Electric Company. All rights reserved, except that this document may be used, copied, and distributed without modification. Neither Pacific Gas and Electric Company, Southern California Edison, San Diego Gas & Electric Company, or any of its employees make any warranty, express or implied; or assume any legal liability or responsibility for the accuracy, completeness or usefulness of any data, information, method, product, policy or process disclosed in this document; or represent that its use will not infringe any privately-owned rights including, but not limited to, patents, trademarks or copyrights.
Introduction
This spreadsheet was developed to aid in calculation of Room Load and of determination of whether or not the Space Conditioning equipment in the design is adequate to meet the load and whether or not it meets all the proposed prescriptive requirements.
Purpose of This Tool
This spreadsheet implements the load calculation and equipment sizing methodology described in Appendix NA9 of the Title 24 Draft CASE Report for Controlled Environment Horticulture (CEH).
The purpose of this tool is to:
Calculate CEH room sensible and latent loads at four prescribed operating conditions.
Collect system performance data at those same four conditions.
Provide simple checks and data that code officials can use for compliance and verification.
Determine whether proposed integrated or decoupled space conditioning systems meet proposed mandatory sizing requirements:
  Meets total cooling load at all four conditions
  Meets total latent removal load at all four conditions
  Provides sufficient cooling and dehumidification capacity
This procedure applies to:
CEH spaces with lighting power density > 30 W per canopy square foot, and
Facilities with canopy area ≥ 5,000 ft².
Overview of the Four Required Operating Conditions
The load and system performance must be avaluated for lights on (day) and lights off (night) conditions for each of two stages: early/mid (weeks 3-6), and late (final week). This totals four required design conditions.
All load calculations and equipment performance inputs must corespond to:
The specified room dry bulb and wet bulb conditions
The specified grow cycle stage
The specified lights-on or lights-off condition
The Summer Design Outdoor Condition (0.4%)
Overview of Required Inputs
User provides:
Room and canopy square footage
Wet bulb and dry bulb design conditions at each of four points in the grow cycle
Environmental load conditions at each of those four points
Automated Calculations
Based on user inputs, the tool automatically calculates:
Feedback on the Proposed Load and Sizing Calculations
The Statewide CASE Team is requesting feedback on the proposed Indoor CEH load and sizing calculations for indoor (<50% skylight ratio) CEH facilities that include a room with lighting power density greater than 30 Watts per canopy square foot. We invite participation from new and existing stakeholders.
Please send an email to adroitcour@westmonroe.com or gtorvestad@westmonroe.com and copy info@title24stakeholders.com with feedback or to set up a meeting to discuss feedback.

## Integrated Load and Sizing Calc
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
For each room with at least 30w/sf of canopy, prepare the following performance matrix.
Facility Ambient Design Conditions
Key
ASHRAE WMO Station: |  |  | User Input Value
Summer Design (0.4%) | DB (°F) |  | Default no value |  | 0
| MCWB (°F) |  | Calculated Value
Winter Design (99%): | DB (°F) |  | Day=Lights On; Night=Lights Off
Facility Room Details
Fill out the following for each room/CEH Space
Room Name: |  |  |  | (Can be multiple rooms of the same size)
Canopy Square Feet:
Provide the Design Space Conditions for the four CEH environment operating conditions:
|  | Early/Mid Plant Life |  | Late Plant Life
|  | Day | Night | Day | Night
Room Conditions (Setpoints) | DB (°F)
WB (°F)
Relative Humidity | %RH
CEH Room Load Calc
Provide the CEH Environmental Load Requirements for each space at the 4 prescribed conditions: | [5 empty] | Check Operation: | Conversions & Calculations | [6 empty] | Check question | Resp.
|  | Early/Mid Plant Life |  | Late Plant Life |  |  |  |  | Early Plant Life |  | Late Plant Life
|  | Day | Night | Day | Night |  |  |  | Day | Night | Day | Night
Horticultural Lighting | (kW) |  |  |  |  | Convert -> |  |  | 0 | 0 | 0 | 0 | BTU/hr
Motor Heat (Fan Power) | (kW) |  |  |  |  | Convert -> |  |  | 0 | 0 | 0 | 0 | BTU/hr
Standalone Dehu Load | (BTU/hr) | 0 | 0 | 0 | 0
Envelope Load (Optional) | (BTU/hr)
Plant Irrigation (total minus runoff) | (gal/day) |  |  |  | 0 | Convert> | [6 empty] | lb/day
% of Net Irrigation Transpired Day/Night | % |  | 100% |  | 100%
Hours (Day/Night) | (hrs) |  | 24 |  | 24 | Calc -> |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | lb/hr
Sensible Space Load | (BTU/hr) | 0 | 0 | 0 | 0 | <- Calc
Evapotranspiration Load | (BTU/hr) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | <- Calc
Mandatory Compliance and Cooling System Operating Performance Information
Integrated System Equipment Specification | [5 empty] | Check Operation: | Conversions & Calculations | [6 empty] | Check question for mandatory requirements on integrated systems. | Resp.
Input the Primary System Performance Information that corresponds to the ambient and CEH space operating conditions and loads above:
|  | Early/Mid Plant Life |  | Late Plant Life
|  | Day | Night | Day | Night |  | Min | Max
System Operating Air Flow | (CFM) |  |  |  |  | Min/Max -> | 0 | 0 | [5 empty] | Does the system have variable air flow? | Invalid or missing input | Mandatory
Total Cooling Operating Capacity | (BTU/hr) |  |  |  |  | Compare -> |  |  | Invalid or missing input | Invalid or missing input | Invalid or missing input | Invalid or missing input |  | Is the total cooling capacity at each condition at least 80% of the total? | Invalid or missing input | Mandatory
Latent Removal Operating Capacity | (BTU/hr) |  |  |  |  | Compare -> |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Is the total latent removal capacity at each condition at least 80% of the total? | Invalid or missing input | Mandatory
Operating Sensible Heat Ratio |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Min/Max -> | #DIV/0! | #DIV/0!
Reheat Operating Load | (BTU/hr)
Recovered Heat Operating Capacity | (BTU/hr) |  |  |  |  | Calc -> |  |  | Invalid or missing input | Invalid or missing input | Invalid or missing input | Invalid or missing input |  | Does the system recover at least 90% of the reheat requirement? | Invalid or missing input | Mandatory
Source of Recovered Heat | Type
Number of Cooling Stages | (#)
Cooling Stage # Type |  | Constant
"Operating" Loads and Capacities mean those operating loads on the system at the design CEH space conditions at the Summer Design Outdoor Conditions.
Additional Equipment Specification
|  | Early/Mid Plant Life |  | Late Plant Life |  | Check Operation: | Conversions & Calculations | [6 empty] | Check question | Resp.
|  | Day | Night | Day | Night
Quantity of Standalone Dehumidifiers | (#) |  | 0 |  | 0
Rated Moisture Removal Capacity | (pints/day) |  | 0 |  | 0
Moisture Removal Capacity (At operating conditions) | (pints/day) | 0 | 0 | 0 | 0 | Convert -> |  |  | 0 | 0 | 0 | 0 | lb/hr
Rated Standalone Dehumidifier Moisture Removal Efficiency @ 80F/60% RH | (L/kWh)
Standalone Dehumidifier Moisture Removal Efficiency | (L/kWh) | 0 | 0 | 0 | 0
Standalone Dehumidifier Motor Power | (kW/ea)
Total Hourly Moisture Removal Capacity | (lbm/hr) | 0 | 0 | 0 | 0
Supplemental Heating Capacity | (BTU/hr) |  |  |  |  | Compare ->
Supplemental Heating Source | Text Input
Mandatory Sizing Requirements - All System Types
System Summary (including Standalone and Supplemental Heat) | [5 empty] | Check Operation: | [7 empty] | Check question | Resp.
|  | Early/Mid Plant Life |  | Late Plant Life
|  | Day | Night | Day | Night
Total System Cooling Capacity | (BTU/hr) | 0 | 0 | 0 | 0 | Compare -> |  |  | 0 | 0 | 0 | 0 |  | Does the system have enough cooling capacity? (Positive = Yes) | Invalid or missing inputs | mandatory
Total Latent Removal Capacity | (BTU/hr) | 0 | 0 | 0 | 0 | Compare -> |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Does the system have enough moisture removal capacity? (Positive = Yes) | Invalid or missing input | mandatory
"Operating" Loads mean those operating loads on the system at the design CEH space conditions at the Summer Design Outdoor Conditions.
Compliance Summary
Does this meet mandatory performance requirements? | Invalid or missing inputs
Does this meet mandatory sizing requirements? | Invalid or missing inputs

## Decoupled Load and Sizing
This Draft Document was developed by the Statewide Utility Codes and Standards Enhancement Team. Please see the Read Me Tab for more information.
For each room with at least 30w/sf of canopy, prepare the following performance matrix.
Facility Ambient Design Conditions
Key
ASHRAE WMO Station: |  |  | User Input Value
Summer Design (0.4%) | DB (°F) |  | Default no value |  | 0
| MCWB (°F) |  | Calculated Value
Winter Design (99%): | DB (°F) |  | Day=Lights On; Night=Lights Off
Facility Room Details
Fill out the following for each room/CEH Space
Room Name: |  |  |  | (Can be multiple rooms of the same size)
Canopy Square Feet:
Provide the Design Space Conditions for the four CEH environment operating conditions:
|  | Early/Mid Plant Life |  | Late Plant Life
|  | Day | Night | Day | Night
Room Conditions (Setpoints) | DB (°F)
WB (°F)
Relative Humidity | %RH
CEH Room Load Calc
Provide the CEH Environmental Load Requirements for each space at the 4 prescribed conditions: | [5 empty] | Check Operation: | Conversions & Calculations | [6 empty] | Check question | Resp.
|  | Early/Mid Plant Life |  | Late Plant Life |  |  |  |  | Early/Mid Plant Life |  | Late Plant Life
|  | Day | Night | Day | Night |  |  |  | Day | Night | Day | Night
Horticultural Lighting | (kW) |  |  |  |  | Convert -> |  |  | 0 | 0 | 0 | 0 | BTU/hr
Motor Heat (Fan Power) | (kW) |  |  |  |  | Convert -> |  |  | 0 | 0 | 0 | 0 | BTU/hr
Standalone Dehu Load | (BTU/hr) | 0 | 0 | 0 | 0
Envelope Load (Optional) | (BTU/hr)
Plant Irrigation | (gal/day) |  |  |  |  | Convert -> | [6 empty] | lb/day
% of Total Irrigation Transpired | % |  | 100% |  | 100% | Check ->
Hours (Day/Night) | (hrs) |  | 24 |  | 24 | Calc -> |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | lb/hr
Sensible Space Load | (BTU/hr) | 0 | 0 | 0 | 0 | <- Calc
Evapotranspiration Load | (BTU/hr) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | <- Calc
Cooling System Operating Performance Information
Non-Integrated Cooling System Equipment Specification | [5 empty] | Check Operation: | Conversions & Calculations | [6 empty] | Check question | Resp.
Input the Cooling System Performance Information that corresponds to the ambient and CEH space operating conditions and loads above:
|  | Early/Mid Plant Life |  | Late Plant Life
|  | Day | Night | Day | Night |  | Min | Max
System Operating Air Flow | (CFM) |  |  |  |  | Min/Max -> | 0 | 0
Total Cooling Operating Capacity | (BTU/hr) |  |  |  |  | Compare -> |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Latent Removal Operating Capacity | (BTU/hr) |  |  |  |  | Compare -> |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Operating Sensible Heat Ratio |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Min/Max -> | #DIV/0! | #DIV/0!
Number of Cooling Stages | (#) |  |  |  |  | Check -> | [7 empty] | Are there at least 2 cooling stages? | Invalid or missing input | Mandatory
Cooling Stage # Type
"Operating" Loads and Capacities mean those operating loads on the system at the design CEH space conditions at the Summer Design Outdoor Conditions.
Additional Equipment Specification
|  | Early/Mid Plant Life |  | Late Plant Life |  | Check Operation: | Conversions & Calculations | [6 empty] | Check question | Resp.
|  | Day | Night | Day | Night
Quantity of Standalone Dehumidifiers | (#) |  | 0 |  | 0
Rated Moisture Removal Capacity @ 80F/60% RH | (pints/day) |  | 0 |  | 0
Moisture Removal Capacity (At operating conditions) | (pints/day) | 0 | 0 | 0 | 0 | Convert -> |  |  | 0 | 0 | 0 | 0 | lb/hr
Rated Standalone Dehumidifier Moisture Removal Efficiency @ 80F/60% RH | (L/kWh)
Standalone Dehumidifier Moisture Removal Efficiency | (L/kWh) | 0 | 0 | 0 | 0
Standalone Dehumidifier Motor Power | (kW/ea)
Total Hourly Moisture Removal Capacity | (lbm/hr) | 0 | 0 | 0 | 0
Supplemental Heating Capacity | (BTU/hr) |  |  |  |  | Compare ->
Supplemental Heating Source | Text Input
Mandatory Sizing Requirements - All System Types
System Summary (including Standalone and Supplemental Heat) | [5 empty] | Check Operation: | [7 empty] | Check question | Resp.
|  | Early/Mid Plant Life |  | Late Plant Life
|  | Day | Night | Day | Night
Total System Cooling Capacity | (BTU/hr) | 0 | 0 | 0 | 0 | Compare -> |  |  | 0 | 0 | 0 | 0 |  | Does the system have enough cooling capacity? (Positive = Yes) | Invalid or missing inputs | mandatory
Total Latent Removal Capacity | (BTU/hr) | 0 | 0 | 0 | 0 | Compare -> |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Does the system have enough moisture removal capacity? (Positive = Yes) | Invalid or missing inputs | mandatory
"Operating" Loads mean those operating loads on the system at the design CEH space conditions at the Summer Design Outdoor Conditions.
Compliance Summary
Does this meet mandatory performance requirements? | Invalid or missing inputs
Does this meet mandatory sizing requirements? | Invalid or missing inputs
Note on G30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Poss delete.

## ComCheck Style (MG - LiqDes) (hidden)
For each room over 30w/sf, prepare the following performance matrix.
User Input Value
Facility Ambient Design Conditions: | [7 empty] | 0 | Default no value
ASHRAE WMO Station: |  | 726357 | [6 empty] | Calculated Value
Summer Design (0.4%) | DB | 90.1 | °F
| MCWB | 72.9 | °F
Winter Design (99%): | DB | 7.5 | °F
The following for each room/CEH Space
Room Name: | Flower 1 |  |  | (Can be multiple rooms of the same size)
Canopy Square Feet: | 1120 | csf
Provide the Design Space Conditions for the four CEH environment operating conditions:
|  | Early Plant Life |  | Late Plant Life
|  | Day | Night | Day | Night
Room Conditions | DB (°F) | 82 | 82 | 68 | 68
| WB (°F) | 73.7 | 73.7 | 55.5 | 55.5
CEH Room Load Calc
Provide the CEH Environmental Load Requirements for each space at the 4 prescribed conditions: | [5 empty] | ComCheck Operation: | Conversions & Calculations | [6 empty] | Check question | Resp.
|  | Early Plant Life |  | Late Plant Life |  |  |  |  | Early Plant Life |  | Late Plant Life
|  | Day | Night | Day | Night |  |  |  | Day | Night | Day | Night
Horticultural Lighting | (kW) | 27.72 | 0 | 52.29 | 0 | Convert -> |  |  | 94663.8 | 0 | 178570.35 | 0 | BTU/hr
Motor Heat (Fan Power) | (kW) | 0 | 0 | 0 | 0 | Convert -> |  |  | 0 | 0 | 0 | 0 | BTU/hr
Standalone Dehu Load | (BTU/hr) | 0
Envelope Load (Optional) | (BTU/hr) | 0 | 0 | 0 | 0
Plant Irrigation | (gal/day) | 202.5 |  | 225 |  | Convert -> |  |  | 1686.825 |  | 1874.25 |  | lbm/day | Does Late Plant life have more irrigation than early plant life? | Y/N
% of Total Irrigation day or night | % | 85% | 15% | 90% | 10%
Lighting Hours (Day/Night) | (hrs) | 12 | 12 | 12 | 12 | Calc -> |  |  | 119.4834 | 21.0853 | 140.5687 | 15.6187 | lb/hr
Sensible Space Load | (BTU/hr) | 94663.8 | 0 | 178570.35 | 0 | <- Calc
Evapotranspiration Load | (BTU/hr) | 126652.4437 | 22350.4313 | 149002.875 | 16555.875 | <- Calc
DO NOT ADD SENSIBLE AND ET LOAD FOR TOTAL LOAD
Prescriptive Compliance and Cooling System Operating Performance Information
Cooling/Integrated System Equipment Specification | [5 empty] | ComCheck Operation:
Input the Primary System Performance Information that corresponds to the ambient and CEH space operating conditions and loads above:
|  | Early Plant Life |  | Late Plant Life
|  | Day | Night | Day | Night |  | Min | Max
System Operating Air Flow | (CFM) | 2000 | 2000 | 2000 | 2000 | Min/Max -> | 2000 | 2000 | [5 empty] | Does the system have variable air flow? | Y/N | Values not equal to eachother
Total Cooling Operating Load | (BTU/hr) | 221316 | 22350 | 327573 | 16556 | Compare -> |  |  | 145584.96 | 22350 | 184716.72 | 16556 |  | Is the total cooling capacity at each condition at least 80% of the total? | Y/N | If its positive
Latent Removal Operating Load | (BTU/hr) | 126652 | 22350 | 149003 | 16556 | Compare -> |  |  | 25330.045 | 4469.655 | 29800.7 | 3311.3 |  | Is the total latent removal capacity at each condition at least 80% of the total? | Y/N | If its positive
Operating Sensible Heat Ratio |  | 0.42773 | 0 | 0.54513 | 0 | Min/Max -> | 0 | 0.54513 | [5 empty] | Is the SHR less than 0.45 at atleast one condition? | Y/N | If any of these values are below 0.45
Reheat Operating Load | (BTU/hr) | 31989 | 22350 | 0 | 16556
Recovered Heat Operating Capacity | (BTU/hr) | 0 | 0 | 0 | 0 | Calc -> |  |  | 0% | 0% | #DIV/0! | 0% |  | Does the system recover at least 90% of the reheat requirement? | Y/N | 90 or above (Y)
Source of Recovered heat:
Cooling Stages:
Cooling Stage # Type:
"Operating" Loads mean those operating loads on the system at the design CEH space conditions at the Summer Design Outdoor Conditions.
Additional Equipment Specification
|  | Early Plant Life |  | Late Plant Life
|  | Day | Night | Day | Night
Quantity of Standalone Dehumidifiers | (qty Ea.) | 0 | 0 | 0 | 0
Moisture removal capacity (At Operating Conditions) | (pints/day) |  |  |  |  | Convert -> |  |  | 0 | 0 | 0 | 0 | lbm/hr
Standalone dehumidifier moisture removal efficiency | (L/kWh) | [12 empty] | Meets federal minimum standard (2.41l/kWh) | Y/N
Standalone Motor Power | (kW/ea)
Total Hourly Moisture Removal Capacity | (lbm/hr) | 0 | 0 | 0 | 0
Supplemental heating capacity | (BTU/hr) | 0 |  |  |  | Compare -> |  |  | 3198.9 | 2235 | 0 | 1655.6
Supplimental heating Capcity Source | Text or Selection
Mandatory Sizing Requirements - All System Types
System Summary (including Standalone and Supplimental Heat)
|  | Early Plant Life |  | Late Plant Life
|  | Day | Night | Day | Night
Total System Cooling Capacity | (BTU/hr) | 221316 | 22350 | 327573 | 16556 | Compare -> |  |  | 126652.2 | 22350 | 149002.65 | 16556 |  | Does the system have enough cooling capacity? (Positive = Yes) | Y/N
Total System Latent Removal Capacity | (BTU/hr) | 126652 | 22350 | 149003 | 16556 | Compare -> |  |  | -0.44375 | -0.43125 | 0.125 | 0.125 |  | Does the system have enough moisture removal capacity? (Positive = Yes) | Y/N
"Operating" Loads mean those operating loads on the system at the design CEH space conditions at the Summer Design Outdoor Conditions.
Note on A41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This should be total capacity
Note on A42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Latent capacity
Note on A44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should the reheat load be calculated?